## Overview
Overview of Siemens Drives with a combination of Schaffner Filters (Input and Output), please click on the links below for further details
| 200VAC -240VAC | 380VAC-480VAC | 500VAC-690VAC
G120 | G120 | G120 | G120
G120C |  | G120C
G120X | G120X | G120X | G120X
G220 | G220 | G220
| Before using you must read our remarks |  | Remarks
| and accept our general disclamer |  | Disclaimer

## Remarks
General remarks on the filter selection
All filter selections are made by calculation of the worst case scenario, covering the maximum drive overload during the maximum allowed duration. In most cases the selection will be oversized and can be downsized according to the application, drive settings and exact parameters of the complete system.
The filter selection is covering only the usage of one filter type per drive. Other combinasion, like one filter for several drives and the mix of passive filter with active harmonic filter (AHF) is not covered in this selection.
The selection of input filters can be confirmed by a simulation using the free Power Quality Simulation (PQS) tool offered by Schaffner.
https://pqs.schaffner.com
For further support please contact your local Siemens and/or Schaffner respresentative.
Remarks Low Leakage applications
All capacitors to earth (referred to as Y capacitors) in the internal EMC filters of the motor drive should be interrupted, as these capacitors can generate additional leakage currents. Drives with built-in EMC filters are not recommended e.g. with low leakage filters.
Remarks EMC/EMI Filters
All suggested Schaffner products are recommendations. The final suitability can be guaranteed only by a measurement in the application and is part of the responsibility of the customer. The information of the limit value class C1 or C2 covers only the conducted emission. The Drive Options, which are not produced by SIEMENS itself, nevertheless the manufacturer have a processual certification from SIEMENS, no liability is assumed by SIEMENS.
Remarks for 200 V Passive Harmonics and Output Filters
The final filter suitability can only be guaranteed in terms of a measurement within the application and is part of the responsibility of the customer. All suggested Schaffner products are recommendations only.
Please be aware that dv/dt filters do only work on differential mode.
For those Drive Options that are not produced by SIEMENS itself, but manufacturer has a processual certification of SIEMENS, no liability is assumed by SIEMENS.
Remarks for 400 V Passive Harmonics and Output Filters
The final filter suitability can only be guaranteed in terms of a measurement within the application and is part of the responsibility of the customer. All suggested Schaffner products are recommendations only. Please use the document “Remarks for Schaffner Recommendation List” available in the Tools and Tips section of this page for further information.
Please be aware that dv/dt as well as sine wave filters do only work on differential mode. Dv/dt and sine wave filters ensure compliance with the requirements of IEC60034-17 (general purpose motors) for cable length named in the data sheets (screened/unscreened). Sine wave filters additionally do provide a sinusoidal phase-to-phase motor terminal voltage but have very limited effect on common mode.
For those Drive Options that are not produced by SIEMENS itself, but manufacturer has a processual certification of SIEMENS, no liability is assumed by SIEMENS.
Remarks for 690 V Passive Harmonics and Output Filters
The final filter suitability can only be guaranteed in terms of a measurement within the application and is part of the responsibility of the customer. All suggested Schaffner products are recommendations only. Please use the document “Remarks for Schaffner Recommendation List” available in the Tools and Tips section of this page for further information.
Ecosine FN 3410 HV filters from 45 kW on do require motor drives equipped with DC-link choke or the application of a 4% (minimum) AC line choke at the input side of the drive!
Please be aware that dv/dt as well as sine wave filters do only work on differential mode. Dv/dt and sine wave filters ensure compliance with the requirements of IEC60034-25B (inverter duty motors) for cable length named in the data sheets (screened/unscreened). Sine wave filters additionally do provide a sinusoidal phase-to-phase motor terminal voltage but have very limited effect on common mode. For the use of general purpose motors on 690V with dv/dt or sine wave filters Schaffner does strongly recommend to contact Schaffner representative prior to any project in order to verify the suitability of the drive-output filter-motor-combination.
For those Drive Options that are not produced by SIEMENS itself, but manufacturer has a processual certification of SIEMENS, no liability is assumed by SIEMENS..

## Disclaimer
DISCLAIMER
BY VISITING THE SCHAFFNER GROUP WEBSITE YOU ACKNOWLEDGE THAT YOU HAVE READ AND ACCEPTED THE FOLLOWING TERMS AND CONDITIONS
Schaffner Holding AG maintains this website solely as a service to provide information to interested parties. By visiting the Schaffner Group website you acknowledge that you have read and accepted the following terms and conditions:
1. Limitation of liability
Schaffner Group uses reasonable care to ensure that the information appearing on this website is up to date and accurate. While Schaffner Group takes precautions to prevent the occurrence of error and omissions, the user of this website should not take the accuracy of information for granted but should check directly with Schaffner Group. Accordingly, Schaffner Group does not accept any liability for any loss or damage which may directly or indirectly result from any advice, opinion, information, representation or omission, whether negligent or otherwise, contained in this site. This includes damages to, or viruses that may infect, your computer equipment.
Schaffner Group reserves the right to change, modify, suspend or discontinue any aspect of the site without notice and liability.
2. Forward looking statements
Certain statements on this site, including statements regarding events and financial trend that may affect future operating results, financial position and cash flow of Schaffner Group may constitute forward-looking statements within the meaning of the United States Private Securities Litigation Reform Act of 1995. Forward looking statements frequently, but not always use the words “expects”, “anticipates”, “suggests”, “plans”, “believes” or “intends”, or similar words and/or include statements concerning strategies, goals and plans, or state that certain actions, events or results “will” be taken, occur or be achieved. These forward looking statements involve known and unknown risks, uncertainties and other factors which may cause the performance or results of Schaffner Group to be materially different from any future performance or results expressed or implied by such statements. Forward-looking statements are based on current expectations and Schaffner Group is not obligated to update such information to reflect later events or developments.
3. Intellectual property / Copyrights
The trademarks, symbols and logos (the trademarks) used and displayed on this site are the property of Schaffner Group unless otherwise indicated. They may not be used without the prior express consent of the trademark owner.
The entire content of this website is subject to copyright of Schaffner Group. You may display, reproduce and use the information contained in this website only for your personal purposes. Any other reproduction, retransmission, modification or use of the site’s content is prohibited unless expressly authorized by Schaffner Group.
4. Links to other websites
This site may contain links to other websites for the convenience of the users of this site. Note that any linked websites are not under control of Schaffner Group. Schaffner Group is not responsible for and makes no representations, warranties or conditions concerning the contents of any linked site or any link contained in linked sites.
5. Data privacy protection
Schaffner Group adheres to the regulations set down by the Swiss Federal Law on the Protection of Data. Schaffner Group treats all data obtained via the Internet confidentially. Personal data that has possibly become known by Schaffner Group will be kept secret, privacy will be respected and the information will be used exclusively for the purpose for which it was made known to Schaffner Group. Without corresponding approval, this data will not be made accessible to third parties, nor transferred to such in any form or manner.
6. Jurisdiction
This website is governed by, and is to be interpreted in accordance with Swiss law. Place of jurisdiction is Solothurn / Switzerland.

## G120 200VAC-240VAC
|  | Drive in Low overload (LO) | [5 empty] | Drive in High overload (HO)
G120 200VAC-240VAC | Power Modul Description | PHF 200-240V 50Hz LO | PHF 200-240V 60Hz LO | dv/dt Reactor 0.8% LO | dv/dt Reactor 6% LO | dv/dt Filter LO | SineWave Filter LO | PHF 200V 50Hz HO | PHF 240V 60Hz HO | dv/dt Reactor 0.8% HO | dv/dt Reactor 6% HO | dv/dt Filter HO | SineWave Filter HO | EMC Filter Motor Cable Lenght ≤ 50m Class C1 | EMC Filter Motor Cable Lenght ≤ 50m Class C2 | EMC Filter Low Leakage Current Motor Cable Lenght ≤ 35m Class C2 | EMC Filter for IT Power Networks Class C2 | EMC Filter Motor Cable Lenght > 50m Class C1 | EMC Filter 3-Phase with Neutral for Machine Tools and Low Leakage Current Applications
6SL3210-1PB13-0UL0 | SINAMICS PM240-2 IP20-FSA-U-230V-0.55KW SINAMICS POWER MODULE PM240-2 WITHOUT FILTER WITH BUILT IN BRAKING CHOPPER 1/3AC200-240V +10/-10% 47-63HZ OUTPUT HIGH OVERLOAD: 0,37KW FOR 200% 3S,150% 57S,100% 240S AMBIENT TEMP -10 TO +50 DEG C OUTPUT LOW OVERLOAD: 0,55KW FOR 150% 3S,110% 57S,100% 240S AMBIENT TEMP -10 TO +40 DEG C 196 X 73 X 165 (HXWXD), FSA PROTECTION IP20 WITHOUT CONTROL UNIT AND PANEL APPROVED FOR CU FIRMWARE- VERSION V4.6 | FN3416LV-10-44 | FN3418LV-8-44 | RWK305-4-KL | RWK5420-5.9-88-E0XXT | FN5060-12-84 | FN5420-5.9-44-E2FXT | FN3416LV-10-44 | FN3418LV-8-44 | RWK305-4-KL | RWK5420-5.9-88-E0XXT | FN5060-12-84 | FN5420-5.9-44-E2FXT | FN3288-10-44-C34-R65 | FN3287-10-44-C28-R65 | FN3288-10-44-C21-R65 | FN3288IT-10-44-C34-R65 | FN3120H-25-33 | FN3280H-8-29-69
6SL3210-1PB13-0AL0 | SINAMICS PM240-2 IP20-FSA-A-230V-0.55KW SINAMICS POWER MODULE PM240-2 WITH BUILT IN CL. A FILTER WITH BUILT IN BRAKING CHOPPER 1/3AC200-240V +10/-10% 47-63HZ OUTPUT HIGH OVERLOAD: 0,37KW FOR 200% 3S,150% 57S,100% 240S AMBIENT TEMP -10 TO +50 DEG C OUTPUT LOW OVERLOAD: 0,55KW FOR 150% 3S,110% 57S,100% 240S AMBIENT TEMP -10 TO +40 DEG C 196 X 73 X 165 (HXWXD), FSA PROTECTION IP20 WITHOUT CONTROL UNIT AND PANEL APPROVED FOR CU FIRMWARE- VERSION V4.6 | FN3416LV-10-44 | FN3418LV-8-44 | RWK305-4-KL | RWK5420-5.9-88-E0XXT | FN5060-12-84 | FN5420-5.9-44-E2FXT | FN3416LV-10-44 | FN3418LV-8-44 | RWK305-4-KL | RWK5420-5.9-88-E0XXT | FN5060-12-84 | FN5420-5.9-44-E2FXT | FN3288-10-44-C34-R65 | FN3287-10-44-C28-R65 | FN3288-10-44-C21-R65 | FN3288IT-10-44-C34-R65 | FN3120H-25-33 | FN3280H-8-29-69
6SL3210 -1PB13-8UL0 | SINAMICS PM240-2 IP20-FSA-U-230V-0.75KW | FN3416LV-10-44 | FN3418LV-8-44 | RWK305-7.8-KL | RWK5420-5.9-88-E0XXT | FN5060-12-84 | FN5420-5.9-44-E2FXT | FN3416LV-10-44 | FN3418LV-8-44 | RWK305-7.8-KL | RWK5420-5.9-88-E0XXT | FN5060-12-84 | FN5420-5.9-44-E2FXT | FN3288-10-44-C34-R65 | FN3287-10-44-C28-R65 | FN3288-10-44-C21-R65 | FN3288IT-10-44-C34-R65 | FN3120H-25-33 | FN3280H-8-29-69
6SL3211 -1PB13-8UL0 | SINAMICS PM240-2 PT-FSA-U-230V-0.75KW | FN3416LV-10-44 | FN3418LV-8-44 | RWK305-7.8-KL | RWK5420-5.9-88-E0XXT | FN5060-12-84 | FN5420-5.9-44-E2FXT | FN3416LV-10-44 | FN3418LV-8-44 | RWK305-7.8-KL | RWK5420-5.9-88-E0XXT | FN5060-12-84 | FN5420-5.9-44-E2FXT | FN3288-10-44-C34-R65 | FN3287-10-44-C28-R65 | FN3288-10-44-C21-R65 | FN3288IT-10-44-C34-R65 | FN3120H-25-33 | FN3280H-8-29-69
6SL3210 -1PB13-8AL0 | SINAMICS PM240-2 IP20-FSA-A-230V-0.75KW | FN3416LV-10-44 | FN3418LV-8-44 | RWK305-7.8-KL | RWK5420-5.9-88-E0XXT | FN5060-12-84 | FN5420-5.9-44-E2FXT | FN3416LV-10-44 | FN3418LV-8-44 | RWK305-7.8-KL | RWK5420-5.9-88-E0XXT | FN5060-12-84 | FN5420-5.9-44-E2FXT | FN3288-10-44-C34-R65 | FN3287-10-44-C28-R65 | FN3288-10-44-C21-R65 | FN3288IT-10-44-C34-R65 | FN3120H-25-33 | FN3280H-8-29-69
6SL3211 -1PB13-8AL0 | SINAMICS PM240-2 PT-FSA-A-230V-0.75KW | FN3416LV-10-44 | FN3418LV-8-44 | RWK305-7.8-KL | RWK5420-5.9-88-E0XXT | FN5060-12-84 | FN5420-5.9-44-E2FXT | FN3416LV-10-44 | FN3418LV-8-44 | RWK305-7.8-KL | RWK5420-5.9-88-E0XXT | FN5060-12-84 | FN5420-5.9-44-E2FXT | FN3288-10-44-C34-R65 | FN3287-10-44-C28-R65 | FN3288-10-44-C21-R65 | FN3288IT-10-44-C34-R65 | FN3120H-25-33 | FN3280H-8-29-69
6SL3210-1PB15-5UL0 | SINAMICS PM240-2 IP20-FSB-U-230V-1.1KW | FN3416LV-10-44 | FN3418LV-8-44 | RWK305-7.8-KL | RWK5420-10-88-E0XXT | FN5060-12-84 | FN5420-10-44-E2FXT | FN3416LV-10-44 | FN3418LV-8-44 | RWK305-7.8-KL | RWK5420-10-88-E0XXT | FN5060-12-84 | FN5420-10-44-E2FXT | FN3288-10-44-C34-R65 | FN3287-10-44-C28-R65 | FN3288-10-44-C21-R65 | FN3288IT-10-44-C34-R65 | FN3120H-25-33 | FN3280H-8-29-69
6SL3210-1PB15-5AL0 | SINAMICS PM240-2 IP20-FSB-A-230V-1.1KW | FN3416LV-10-44 | FN3418LV-8-44 | RWK305-7.8-KL | RWK5420-10-88-E0XXT | FN5060-12-84 | FN5420-10-44-E2FXT | FN3416LV-10-44 | FN3418LV-8-44 | RWK305-7.8-KL | RWK5420-10-88-E0XXT | FN5060-12-84 | FN5420-10-44-E2FXT | FN3288-10-44-C34-R65 | FN3287-10-44-C28-R65 | FN3288-10-44-C21-R65 | FN3288IT-10-44-C34-R65 | FN3120H-25-33 | FN3280H-8-29-69
6SL3210-1PB17-4UL0 | SINAMICS PM240-2 IP20-FSB-U-230V-1.5KW | FN3416LV-10-44 | FN3418LV-11-44 | RWK305-10-KL | RWK5420-10-88-E0XXT | FN5060-12-84 | FN5420-10-44-E2FXT | FN3416LV-10-44 | FN3418LV-11-44 | RWK305-10-KL | RWK5420-10-88-E0XXT | FN5060-12-84 | FN5420-10-44-E2FXT | FN3288-10-44-C34-R65 | FN3287-10-44-C28-R65 | FN3288-10-44-C21-R65 | FN3288IT-10-44-C34-R65 | FN3120H-25-33 | FN3280H-16-29-69
6SL3210-1PB17-4AL0 | SINAMICS PM240-2 IP20-FSB-A-230V-1.5KW | FN3416LV-10-44 | FN3418LV-11-44 | RWK305-10-KL | RWK5420-10-88-E0XXT | FN5060-12-84 | FN5420-10-44-E2FXT | FN3416LV-10-44 | FN3418LV-11-44 | RWK305-10-KL | RWK5420-10-88-E0XXT | FN5060-12-84 | FN5420-10-44-E2FXT | FN3288-10-44-C34-R65 | FN3287-10-44-C28-R65 | FN3288-10-44-C21-R65 | FN3288IT-10-44-C34-R65 | FN3120H-25-33 | FN3280H-16-29-69
6SL3210-1PB21-0UL0 | SINAMICS PM240-2 IP20-FSB-U-230V-2.2KW | FN3416LV-16-44 | FN3418LV-15-44 | RWK305-14-KL | RWK5420-13-89-E0XXT | FN5060-12-84 | FN5420-13-33-E2FXT | FN3416LV-16-44 | FN3418LV-15-44 | RWK305-14-KL | RWK5420-13-89-E0XXT | FN5060-12-84 | FN5420-13-33-E2FXT | FN3288-16-44-C35-R65 | FN3287-16-44-C33-R65 | FN3288-16-44-C21-R65 | FN3288IT-16-44-C34-R65 | FN3120H-25-33 | FN3280H-16-29-69
6SL3211 -1PB21-0UL0 | SINAMICS PM240-2 PT-FSB-U-230V-2.2KW SINAMICS POWER MODULE PM240-2 WITHOUT FILTER WITH BUILT IN BRAKING CHOPPER 1/3AC200-240V +10/-10% 47-63HZ OUTPUT HIGH OVERLOAD: 1,5KW FOR 200% 3S,150% 57S,100% 240S AMBIENT TEMP -10 TO +50 DEG C OUTPUT LOW OVERLOAD: 2,2KW FOR 150% 3S,110% 57S,100% 240S AMBIENT TEMP -10 TO +40 DEG C 345 X 154 X 171 (HXWXD), FSB PROTECTION IP20-PT WITHOUT CONTROL UNIT AND PANEL APPROVED FOR CU FIRMWARE- VERSION V4.6 | FN3416LV-16-44 | FN3418LV-15-44 | RWK305-14-KL | RWK5420-13-89-E0XXT | FN5060-12-84 | FN5420-13-33-E2FXT | FN3416LV-16-44 | FN3418LV-15-44 | RWK305-14-KL | RWK5420-13-89-E0XXT | FN5060-12-84 | FN5420-13-33-E2FXT | FN3288-16-44-C35-R65 | FN3287-16-44-C33-R65 | FN3288-16-44-C21-R65 | FN3288IT-16-44-C34-R65 | FN3120H-25-33 | FN3280H-16-29-69
6SL3210 -1PB21-0AL0 | SINAMICS PM240-2 IP20-FSB-A-230V-2.2KW | FN3416LV-16-44 | FN3418LV-15-44 | RWK305-14-KL | RWK5420-13-89-E0XXT | FN5060-12-84 | FN5420-13-33-E2FXT | FN3416LV-16-44 | FN3418LV-15-44 | RWK305-14-KL | RWK5420-13-89-E0XXT | FN5060-12-84 | FN5420-13-33-E2FXT | FN3288-16-44-C35-R65 | FN3287-16-44-C33-R65 | FN3288-16-44-C21-R65 | FN3288IT-16-44-C34-R65 | FN3120H-25-33 | FN3280H-16-29-69
6SL3211 -1PB21-0AL0 | SINAMICS PM240-2 IP20-FSC-U-230V-3KW | FN3416LV-16-44 | FN3418LV-15-44 | RWK305-14-KL | RWK5420-13-89-E0XXT | FN5060-12-84 | FN5420-13-33-E2FXT | FN3416LV-16-44 | FN3418LV-15-44 | RWK305-14-KL | RWK5420-13-89-E0XXT | FN5060-12-84 | FN5420-13-33-E2FXT | FN3288-16-44-C35-R65 | FN3287-16-44-C33-R65 | FN3288-16-44-C21-R65 | FN3288IT-16-44-C34-R65 | FN3120H-25-33 | FN3280H-16-29-69
6SL3210-1PB21-4UL0 | SINAMICS PM240-2 IP20-FSC-U-230V-3KW | FN3416LV-24-33 | FN3418LV-21-33 | RWK305-17-KL | RWK5420-18-89-E0XXT | FN5060-24-84 | FN5420-18-33-E2FXT | FN3416LV-24-33 | FN3418LV-21-33 | RWK305-17-KL | RWK5420-18-89-E0XXT | FN5060-24-84 | FN5420-18-33-E2FXT | FN3288-20-33-C35-R65 | FN3287-20-33-C33-R65 | FN3288-20-33-C21-R65 | FN3288IT-20-33-C34-R65 | FN3120H-25-33 | FN3280H-25-33-69
6SL3210-1PB21-4AL0 | SINAMICS PM240-2 IP20-FSC-A-230V-3KW | FN3416LV-24-33 | FN3418LV-21-33 | RWK305-17-KL | RWK5420-18-89-E0XXT | FN5060-24-84 | FN5420-18-33-E2FXT | FN3416LV-24-33 | FN3418LV-21-33 | RWK305-17-KL | RWK5420-18-89-E0XXT | FN5060-24-84 | FN5420-18-33-E2FXT | FN3288-20-33-C35-R65 | FN3287-20-33-C33-R65 | FN3288-20-33-C21-R65 | FN3288IT-20-33-C34-R65 | FN3120H-25-33 | FN3280H-25-33-69
6SL3210 -1PB21-8UL0 | SINAMICS PM240-2 IP20-FSC-U-230V-4KW | FN3416LV-32-33 | FN3418LV-28-33 | RWK305-24-KL | RWK5420-26-92-E0XXT | FN5060-24-84 | FN5420-26-33-E2FXT | FN3416LV-32-33 | FN3418LV-28-33 | RWK305-24-KL | RWK5420-26-92-E0XXT | FN5060-24-84 | FN5420-26-33-E2FXT | FN3288-25-33-C35-R65 | FN3287-25-33-C33-R65 | FN3288-25-33-C21-R65 | FN3288IT-25-33-C34-R65 | FN3120H-25-33 | FN3280H-25-33-69
6SL3211 -1PB21-8UL0 | SINAMICS PM240-2 PT-FSC-U-230V-4KW | FN3416LV-32-33 | FN3418LV-28-33 | RWK305-24-KL | RWK5420-26-92-E0XXT | FN5060-24-84 | FN5420-26-33-E2FXT | FN3416LV-32-33 | FN3418LV-28-33 | RWK305-24-KL | RWK5420-26-92-E0XXT | FN5060-24-84 | FN5420-26-33-E2FXT | FN3288-25-33-C35-R65 | FN3287-25-33-C33-R65 | FN3288-25-33-C21-R65 | FN3288IT-25-33-C34-R65 | FN3120H-25-33 | FN3280H-25-33-69
6SL3210 -1PB21-8AL0 | SINAMICS PM240-2 IP20-FSC-A-230V-4KW | FN3416LV-32-33 | FN3418LV-28-33 | RWK305-24-KL | RWK5420-26-92-E0XXT | FN5060-24-84 | FN5420-26-33-E2FXT | FN3416LV-32-33 | FN3418LV-28-33 | RWK305-24-KL | RWK5420-26-92-E0XXT | FN5060-24-84 | FN5420-26-33-E2FXT | FN3288-25-33-C35-R65 | FN3287-25-33-C33-R65 | FN3288-25-33-C21-R65 | FN3288IT-25-33-C34-R65 | FN3120H-25-33 | FN3280H-25-33-69
6SL3211 -1PB21-8AL0 | SINAMICS PM240-2 PT-FSC-A-230V-4KW | FN3416LV-32-33 | FN3418LV-28-33 | RWK305-24-KL | RWK5420-26-92-E0XXT | FN5060-24-84 | FN5420-26-33-E2FXT | FN3416LV-32-33 | FN3418LV-28-33 | RWK305-24-KL | RWK5420-26-92-E0XXT | FN5060-24-84 | FN5420-26-33-E2FXT | FN3288-25-33-C35-R65 | FN3287-25-33-C33-R65 | FN3288-25-33-C21-R65 | FN3288IT-25-33-C34-R65 | FN3120H-25-33 | FN3280H-25-33-69
6SL3210-1PC22-2UL0 | SINAMICS PM240-2 IP20-FSC-U-230V-5.5KW | FN3416LV-38-33 | FN3418LV-35-33 | RWK305-24-KL | RWK5420-26-92-E0XXT | FN5060-24-84 | FN5420-26-33-E2FXT | FN3416LV-38-33 | FN3418LV-35-33 | RWK305-32-KL | RWK5420-26-92-E0XXT | FN5060-30-99 | FN5420-26-33-E2FXT | FN3288-40-33-C35-R65 | FN3287-40-33-C33-R65 | FN3288-40-33-C21-R65 | FN3288IT-40-33-C34-R65 | FN3120H-50-53 | FN3280H-36-33-69
6SL3210-1PC22-2AL0 | SINAMICS PM240-2 IP20-FSC-A-230V-5.5KW | FN3416LV-38-33 | FN3418LV-35-33 | RWK305-24-KL | RWK5420-26-92-E0XXT | FN5060-24-84 | FN5420-26-33-E2FXT | FN3416LV-38-33 | FN3418LV-35-33 | RWK305-32-KL | RWK5420-26-92-E0XXT | FN5060-30-99 | FN5420-26-33-E2FXT | FN3288-40-33-C35-R65 | FN3287-40-33-C33-R65 | FN3288-40-33-C21-R65 | FN3288IT-40-33-C34-R65 | FN3120H-50-53 | FN3280H-36-33-69
6SL3210-1PC22-8AL0 | SINAMICS PM240-2 IP20-FSC-A-230V-7.5KW | FN3416LV-45-33 | FN3418LV-41-33 | RWK305-32-KL | RWK5420-32-92-E0XXT | FN5060-45-99 | FN5420-32-33-E2FXT | FN3416LV-38-33 | FN3418LV-41-33 | RWK305-45-KL | RWK5420-38-92-E0XXT | FN5060-45-99 | FN5420-38-33-E2FXT | FN3288-40-33-C35-R65 | FN3287-40-33-C33-R65 | FN3288-40-33-C21-R65 | FN3288IT-40-33-C34-R65 | FN3120H-50-53 | FN3280H-36-33-69
6SL3210-1PC22-8UL0 | SINAMICS PM240-2 IP20-FSC-U-230V-7.5KW | FN3416LV-45-33 | FN3418LV-41-33 | RWK305-32-KL | RWK5420-32-92-E0XXT | FN5060-45-99 | FN5420-32-33-E2FXT | FN3416LV-38-33 | FN3418LV-41-33 | RWK305-45-KL | RWK5420-38-92-E0XXT | FN5060-45-99 | FN5420-38-33-E2FXT | FN3288-40-33-C35-R65 | FN3287-40-33-C33-R65 | FN3288-40-33-C21-R65 | FN3288IT-40-33-C34-R65 | FN3120H-50-53 | FN3280H-36-33-69
6SL3210-1PC24-2UL0 | SINAMICS PM240-2 IP20-FSD-U-200V-11kW | FN3416LV-60-34 | FN3418LV-65-34 | RWK305-60-KL | RWK5420-60-92-E0XXT | FN5060-60-99 | FN5420-60-34-E2FXT | FN3416LV-60-34 | FN3418LV-53-34 | RWK305-60-KL | RWK5420-60-92-E0XXT | FN5060-60-99 | FN5420-60-34-E2FXT | FN3288-40-33-C35-R65 | FN3287-40-33-C33-R65 | FN3288-40-33-C21-R65 | FN3288IT-40-33-C34-R65 | FN3120H-50-53 | FN3280H-64-34-69
6SL3210-1PC25-4UL0 | SINAMICS PM240-2 IP20-FSD-U-200V-15kW | FN3416LV-90-35 | FN3418LV-80-35 | RWK305-60-KL | RWK5420-60-92-E0XXT | FN5060-60-99 | FN5420-60-34-E2FXT | FN3416LV-90-35 | FN3418LV-80-35 | RWK305-72-KL | RWK5420-75-99-E0XXT | FN5060-70-99 | FN5420-75-35-E2FXT | FN3288-50-53-C35-R65 | FN3287-50-53-C33-R65 | FN3288-50-53-C21-R65 | FN3288IT-50-53-C34-R65 | FN3120H-50-53 | FN3280H-64-34-69
6SL3210-1PC26-8UL0 | SINAMICS PM240-2 IP20-FSD-U-200V-18,5kW | FN3416LV-110-35 | FN3418LV-105-35 | RWK305-90-KL | RWK5420-75-99-E0XXT | FN5060-90-99 | FN5420-75-35-E2FXT | FN3416LV-150-40 | FN3418LV-105-35 | RWK305-90-KL | RWK5420-90-99-E0XXT | FN5060-90-99 | FN5420-90-35-E2FXT | FN3288-63-53-C35-R65 | FN3287-63-53-C33-R65 | FN3288-63-53-C21-R65 | FN3288IT-63-53-C34-R65 | FN3120H-80-35 | FN3280H-64-34-69
6SL3210-1PC28-0UL0 | SINAMICS PM240-2 IP20-FSE-U-200V-22kW | FN3416LV-150-40 | FN3418LV-130-40 | RWK305-90-KL | RWK5420-90-99-E0XXT | FN5060-90-99 | FN5420-90-35-E2FXT | FN3416LV-180-40 | FN3418LV-130-40 | RWK305-110-KL | RWK5420-110-99-E0XXT | FN5060-110-99 | FN5420-110-35-E2FXT | FN3288-80-34-C35-R65 | FN3287-80-34-C33-R65 | FN3288-80-34-C21-R65 | FN3288IT-80-34-C34-R65 | FN3120H-80-35 | FN3280H-80-35-69
6SL3210-1PC31-1UL0 | SINAMICS PM240-2 IP20-FSE-U-200V-30kW | FN3416LV-180-40 | FN3418LV-160-40 | RWK305-124-KS | RWK5420-145-99-E0XXT | FN5060-150-99 | FN5420-145-99-E0XXT | FN3416LV-180-40 | FN3418LV-160-40 | RWK305-124-KS | RWK5420-145-99-E0XXT | FN5060-150-99 | FN5420-145-99-E0XXT | FN3288-100-35-C35-R65 | FN3287-100-35-C33-R65 | FN3288-100-35-C21-R65 | FN3288IT-100-35-C34-R65 | FN3120H-110-35 | FN3280H-120-35-69
6SL3210-1PC31-3UL0 | SINAMICS PM240-2 IP20-FSF-U-200V-37kW | FN3416LV-210-40 | FN3418LV-190-40 | RWK305-143-KS | RWK5420-145-99-E0XXT | FN5060-150-99 | FN5420-145-99-E0XXT | FN3416LV-260-99 | FN3418LV-240-99 | RWK305-156-KS | RWK5420-180-99-E0XXT | FN5060-180-99 | FN5420-180-99-E0XXT | FN3288-125-35-C35-R65 | FN3287-125-35-C33-R65 | FN3288-125-35-C21-R65 | FN3288IT-125-35-C34-R65 | FN3120H-150-40 | FN3280H-160-40-69
6SL3210-1PC31-6UL0 | SINAMICS PM240-2 IP20-FSF-U-200V-45kW | FN3416LV-260-99 | FN3418LV-240-99 | RWK305-170-KS | RWK5420-180-99-E0XXT | FN5060-180-99 | FN5420-180-99-E0XXT | FN3416LV-260-99 | FN3418LV-240-99 | RWK305-230-KS | RWK5420-200-99-E0XXT | FN5060-250-99 | FN5420-200-99-E0XXT | FN3288-160-40-C35-R65 | FN3287-160-40-C33-R65 | FN3288-160-40-C21-R65 | FN3288IT-160-40-C34-R65 | FN3120H-230-40 | FN3280H-160-40-69
6SL3210-1PC31-8UL0 | SINAMICS PM240-2 IP20-FSF-U-200V-55kW | FN3416LV-320-99 | FN3418LV-310-99 | RWK305-230-KS | RWK5420-200-99-E0XXT | FN5060-250-99 | FN5420-200-99-E0XXT | 2x FN3416LV-210-40 | FN3418LV-310-99 | RWK305-230-KS | RWK5420-250-99-E0XXT | FN5060-250-99 | FN5420-250-99-E0XXT | FN3288-230-40-C35-R65 | FN3287-230-40-C33-R65 | FN3288-230-40-C21-R65 | FN3288IT-230-40-C34-R65 | FN3120H-230-40 | FN3280H-200-40-69

## G120 380VAC-480VAC
|  | Drive in Low overload (LO) | [12 empty] | Drive in High overload (HO)
G120 380VAC-480VAC | Power Modul Description | PHF 5% THDi 400V 50Hz LO | PHF 5% THDi 480V 50Hz LO | PHF 5% THDi 380V 60Hz LO | PHF 5% THDi 480V 60Hz LO | PHF 10-15% THDi 400V 50Hz LO | PHF 10-15% THDi 480V 50Hz LO | PHF 10-15% THDi 400V 60Hz LO | PHF 10-15% THDi 480V 60Hz LO | AC Line Reactor LO | dv/dt Reactor 0.8% LO | dv/dt Reactor 6% LO | dv/dt Filter LO | SineWave Filter LO | PHF 5% THDi 400V 50Hz HO | PHF 5% THDi 480V 50Hz HO | PHF 5% THDi 400V 60Hz HO | PHF 5% THDi 480V 60Hz HO | PHF 10-15% THDi 400V 50Hz HO | PHF 10-15% THDi 480V 50Hz HO | PHF 10-15% THDi 400V 60Hz HO | PHF 10-15% THDi 480V 60Hz HO | AC Line Reactor HO | dv/dt Reactor 0.8% HO | dv/dt Reactor 6% HO | dv/dt Filter HO | SineWave Filter HO | EMC Filter Motor Cable Lenght ≤ 50m Class C1 | EMC Filter Motor Cable Lenght ≤ 50m Class C2 | EMC Filter Low Leakage Current Motor Cable Lenght ≤ 35m Class C2 | EMC Filter for IT Power Networks Class C2 | EMC Filter Motor Cable Lenght > 50m Class C1 | EMC Filter 3-Phase with Neutral for Machine Tools and Low Leakage Current Applications
6SL3210-1PE11-8UL1 | SINAMICS PM240-2 IP20-FSA-U-400V-0.55KW | FN3440-1-110-E2XXJRX | FN3450-1-110-E2XXJRX | FN3442-1-110-E2XXJRX | FN3452-1-110-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-5-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-2-88-E0XXX | RWK305-4-KL | RWK5420-2.3-88-E0XXT | FN5060-12-84 | FN5420-2.3-44-E2XXT | FN3440-1-110-E2XXJRX | FN3450-1-110-E2XXJRX | FN3442-1-110-E2XXJRX | FN3452-1-110-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-5-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-2-88-E0XXX | RWK305-4-KL | RWK5420-2.3-88-E0XXT | FN5060-12-84 | FN5420-2.3-44-E2XXT | FN3288-10-44-C34-R65 | FN3287-10-44-C28-R65 | FN3288-10-44-C21-R65 | FN3288IT-10-44-C34-R65 | FN3120H-25-33 | FN3280H-8-29-69
6SL3210-1PE11-8AL1 | SINAMICS PM240-2 IP20-FSA-A-400V-0.55KW | FN3440-1-110-E2XXJRX | FN3450-1-110-E2XXJRX | FN3442-1-110-E2XXJRX | FN3452-1-110-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-5-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-2-88-E0XXX | RWK305-4-KL | RWK5420-2.3-88-E0XXT | FN5060-12-84 | FN5420-2.3-44-E2XXT | FN3440-1-110-E2XXJRX | FN3450-1-110-E2XXJRX | FN3442-1-110-E2XXJRX | FN3452-1-110-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-5-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-2-88-E0XXX | RWK305-4-KL | RWK5420-2.3-88-E0XXT | FN5060-12-84 | FN5420-2.3-44-E2XXT | FN3288-10-44-C34-R65 | FN3287-10-44-C28-R65 | FN3288-10-44-C21-R65 | FN3288IT-10-44-C34-R65 | FN3120H-25-33 | FN3280H-8-29-69
6SL3210-1PE12-3UL1 | SINAMICS PM240-2 IP20-FSA-U-400V-0.75KW | FN3440-1-110-E2XXJRX | FN3450-1-110-E2XXJRX | FN3442-1-110-E2XXJRX | FN3452-1-110-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-5-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-2-88-E0XXX | RWK305-4-KL | RWK5420-3.1-88-E0XXT | FN5060-12-84 | FN5420-3.1-44-E2XXT | FN3440-1-110-E2XXJRX | FN3450-1-110-E2XXJRX | FN3442-1-110-E2XXJRX | FN3452-1-110-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-5-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-2-88-E0XXX | RWK305-4-KL | RWK5420-3.1-88-E0XXT | FN5060-12-84 | FN5420-3.1-44-E2XXT | FN3288-10-44-C34-R65 | FN3287-10-44-C28-R65 | FN3288-10-44-C21-R65 | FN3288IT-10-44-C34-R65 | FN3120H-25-33 | FN3280H-8-29-69
6SL3210-1PE12-3AL1 | SINAMICS PM240-2 IP20-FSA-A-400V-0.75KW | FN3440-1-110-E2XXJRX | FN3450-1-110-E2XXJRX | FN3442-1-110-E2XXJRX | FN3452-1-110-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-5-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-2-88-E0XXX | RWK305-4-KL | RWK5420-3.1-88-E0XXT | FN5060-12-84 | FN5420-3.1-44-E2XXT | FN3440-1-110-E2XXJRX | FN3450-1-110-E2XXJRX | FN3442-1-110-E2XXJRX | FN3452-1-110-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-5-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-2-88-E0XXX | RWK305-4-KL | RWK5420-3.1-88-E0XXT | FN5060-12-84 | FN5420-3.1-44-E2XXT | FN3288-10-44-C34-R65 | FN3287-10-44-C28-R65 | FN3288-10-44-C21-R65 | FN3288IT-10-44-C34-R65 | FN3120H-25-33 | FN3280H-8-29-69
6SL3210-1PE13-2UL1 | SINAMICS PM240-2 IP20-FSA-U-400V-1.1KW | FN3440-1-110-E2XXJRX | FN3450-2-110-E2XXJRX | FN3442-2-110-E2XXJRX | FN3452-1-110-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-5-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-3.5-88-E0XXX | RWK305-4-KL | RWK5420-5.9-88-E0XXT | FN5060-12-84 | FN5420-5.9-44-E2FXT | FN3440-1-110-E2XXJRX | FN3450-2-110-E2XXJRX | FN3442-1-110-E2XXJRX | FN3452-1-110-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-5-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-3.5-88-E0XXX | RWK305-4-KL | RWK5420-5.9-88-E0XXT | FN5060-12-84 | FN5420-5.9-44-E2FXT | FN3288-10-44-C34-R65 | FN3287-10-44-C28-R65 | FN3288-10-44-C21-R65 | FN3288IT-10-44-C34-R65 | FN3120H-25-33 | FN3280H-8-29-69
6SL3210-1PE13-2AL1 | SINAMICS PM240-2 IP20-FSA-A-400V-1.1KW | FN3440-1-110-E2XXJRX | FN3450-2-110-E2XXJRX | FN3442-2-110-E2XXJRX | FN3452-1-110-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-5-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-3.5-88-E0XXX | RWK305-4-KL | RWK5420-5.9-88-E0XXT | FN5060-12-84 | FN5420-5.9-44-E2FXT | FN3440-1-110-E2XXJRX | FN3450-2-110-E2XXJRX | FN3442-1-110-E2XXJRX | FN3452-1-110-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-5-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-3.5-88-E0XXX | RWK305-4-KL | RWK5420-5.9-88-E0XXT | FN5060-12-84 | FN5420-5.9-44-E2FXT | FN3288-10-44-C34-R65 | FN3287-10-44-C28-R65 | FN3288-10-44-C21-R65 | FN3288IT-10-44-C34-R65 | FN3120H-25-33 | FN3280H-8-29-69
6SL3210-1PE14-3UL1 | SINAMICS PM240-2 IP20-FSA-U-400V-1.5KW | FN3440-1-110-E2XXJRX | FN3450-2-110-E2XXJRX | FN3442-2-110-E2XXJRX | FN3452-3-110-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-5-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-3.5-88-E0XXX | RWK305-7.8-KL | RWK5420-5.9-88-E0XXT | FN5060-12-84 | FN5420-5.9-44-E2FXT | FN3440-1-110-E2XXJRX | FN3450-2-110-E2XXJRX | FN3442-2-110-E2XXJRX | FN3452-3-110-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-5-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-3.5-88-E0XXX | RWK305-7.8-KL | RWK5420-5.9-88-E0XXT | FN5060-12-84 | FN5420-5.9-44-E2FXT | FN3288-10-44-C34-R65 | FN3287-10-44-C28-R65 | FN3288-10-44-C21-R65 | FN3288IT-10-44-C34-R65 | FN3120H-25-33 | FN3280H-8-29-69
6SL3210-1PE14-3AL1 | SINAMICS PM240-2 IP20-FSA-A-400V-1.5KW | FN3440-1-110-E2XXJRX | FN3450-2-110-E2XXJRX | FN3442-2-110-E2XXJRX | FN3452-3-110-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-5-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-3.5-88-E0XXX | RWK305-7.8-KL | RWK5420-5.9-88-E0XXT | FN5060-12-84 | FN5420-5.9-44-E2FXT | FN3440-1-110-E2XXJRX | FN3450-2-110-E2XXJRX | FN3442-2-110-E2XXJRX | FN3452-3-110-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-5-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-3.5-88-E0XXX | RWK305-7.8-KL | RWK5420-5.9-88-E0XXT | FN5060-12-84 | FN5420-5.9-44-E2FXT | FN3288-10-44-C34-R65 | FN3287-10-44-C28-R65 | FN3288-10-44-C21-R65 | FN3288IT-10-44-C34-R65 | FN3120H-25-33 | FN3280H-8-29-69
6SL3210-1PE16-1UL1 | SINAMICS PM240-2 IP20-FSA-U-400V-2.2KW | FN3440-2-110-E2XXJRX | FN3450-4-112-E2XXJRX | FN3442-4-112-E2XXJRX | FN3452-3-110-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-5-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-6.5-88-E0XXX | RWK305-7.8-KL | RWK5420-10-88-E0XXT | FN5060-12-84 | FN5420-10-44-E2FXT | FN3440-2-110-E2XXJRX | FN3450-4-112-E2XXJRX | FN3442-2-110-E2XXJRX | FN3452-3-110-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-5-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-6.5-88-E0XXX | RWK305-7.8-KL | RWK5420-10-88-E0XXT | FN5060-12-84 | FN5420-10-44-E2FXT | FN3288-10-44-C34-R65 | FN3287-10-44-C28-R65 | FN3288-10-44-C21-R65 | FN3288IT-10-44-C34-R65 | FN3120H-25-33 | FN3280H-8-29-69
6SL3210-1PE16-1AL1 | SINAMICS PM240-2 IP20-FSA-A-400V-2.2KW | FN3440-2-110-E2XXJRX | FN3450-4-112-E2XXJRX | FN3442-4-112-E2XXJRX | FN3452-3-110-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-5-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-6.5-88-E0XXX | RWK305-7.8-KL | RWK5420-10-88-E0XXT | FN5060-12-84 | FN5420-10-44-E2FXT | FN3440-2-110-E2XXJRX | FN3450-4-112-E2XXJRX | FN3442-2-110-E2XXJRX | FN3452-3-110-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-5-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-6.5-88-E0XXX | RWK305-7.8-KL | RWK5420-10-88-E0XXT | FN5060-12-84 | FN5420-10-44-E2FXT | FN3288-10-44-C34-R65 | FN3287-10-44-C28-R65 | FN3288-10-44-C21-R65 | FN3288IT-10-44-C34-R65 | FN3120H-25-33 | FN3280H-8-29-69
6SL3210-1PE18-0UL1 | SINAMICS PM240-2 IP20-FSA-U-400V-3KW | FN3440-4-112-E2XXJRX | FN3450-4-112-E2XXJRX | FN3442-4-112-E2XXJRX | FN3452-5-112-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-5-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-6.5-88-E0XXX | RWK305-10-KL | RWK5420-10-88-E0XXT | FN5060-12-84 | FN5420-10-44-E2FXT | FN3440-4-112-E2XXJRX | FN3450-4-112-E2XXJRX | FN3442-4-112-E2XXJRX | FN3452-5-112-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-5-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-6.5-88-E0XXX | RWK305-10-KL | RWK5420-10-88-E0XXT | FN5060-12-84 | FN5420-10-44-E2FXT | FN3288-10-44-C34-R65 | FN3287-10-44-C28-R65 | FN3288-10-44-C21-R65 | FN3288IT-10-44-C34-R65 | FN3120H-25-33 | FN3280H-16-29-69
6SL3211-1PE18-0UL1 | SINAMICS PM240-2 PT-FSA-U-400V-3KW | FN3440-4-112-E2XXJRX | FN3450-4-112-E2XXJRX | FN3442-4-112-E2XXJRX | FN3452-5-112-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-5-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-6.5-88-E0XXX | RWK305-10-KL | RWK5420-10-88-E0XXT | FN5060-12-84 | FN5420-10-44-E2FXT | FN3440-4-112-E2XXJRX | FN3450-4-112-E2XXJRX | FN3442-4-112-E2XXJRX | FN3452-5-112-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-5-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-6.5-88-E0XXX | RWK305-10-KL | RWK5420-10-88-E0XXT | FN5060-12-84 | FN5420-10-44-E2FXT | FN3288-10-44-C34-R65 | FN3287-10-44-C28-R65 | FN3288-10-44-C21-R65 | FN3288IT-10-44-C34-R65 | FN3120H-25-33 | FN3280H-16-29-69
6SL3210-1PE18-0AL1 | SINAMICS PM240-2 IP20-FSA-A-400V-3KW | FN3440-4-112-E2XXJRX | FN3450-4-112-E2XXJRX | FN3442-4-112-E2XXJRX | FN3452-5-112-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-5-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-6.5-88-E0XXX | RWK305-10-KL | RWK5420-10-88-E0XXT | FN5060-12-84 | FN5420-10-44-E2FXT | FN3440-4-112-E2XXJRX | FN3450-4-112-E2XXJRX | FN3442-4-112-E2XXJRX | FN3452-5-112-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-5-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-6.5-88-E0XXX | RWK305-10-KL | RWK5420-10-88-E0XXT | FN5060-12-84 | FN5420-10-44-E2FXT | FN3288-10-44-C34-R65 | FN3287-10-44-C28-R65 | FN3288-10-44-C21-R65 | FN3288IT-10-44-C34-R65 | FN3120H-25-33 | FN3280H-16-29-69
6SL3211-1PE18-0AL1 | SINAMICS PM240-2 PT-FSA-A-400V-3KW | FN3440-4-112-E2XXJRX | FN3450-4-112-E2XXJRX | FN3442-4-112-E2XXJRX | FN3452-5-112-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-5-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-6.5-88-E0XXX | RWK305-10-KL | RWK5420-10-88-E0XXT | FN5060-12-84 | FN5420-10-44-E2FXT | FN3440-4-112-E2XXJRX | FN3450-4-112-E2XXJRX | FN3442-4-112-E2XXJRX | FN3452-5-112-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-5-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-6.5-88-E0XXX | RWK305-10-KL | RWK5420-10-88-E0XXT | FN5060-12-84 | FN5420-10-44-E2FXT | FN3288-10-44-C34-R65 | FN3287-10-44-C28-R65 | FN3288-10-44-C21-R65 | FN3288IT-10-44-C34-R65 | FN3120H-25-33 | FN3280H-16-29-69
6SL3210-1PE21-1UL0 | SINAMICS PM240-2 IP20-FSB-U-400V-4KW | FN3440-4-112-E2XXJRX | FN3450-6-112-E2XXJRX | FN3442-6-112-E2XXJRX | FN3452-5-112-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-8-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-9-88-E0XXX | RWK305-14-KL | RWK5420-13-89-E0XXT | FN5060-12-84 | FN5420-13-33-E2FXT | FN3440-4-112-E2XXJRX | FN3450-6-112-E2XXJRX | FN3442-6-112-E2XXJRX | FN3452-5-112-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-8-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-9-88-E0XXX | RWK305-14-KL | RWK5420-13-89-E0XXT | FN5060-12-84 | FN5420-13-33-E2FXT | FN3288-16-44-C35-R65 | FN3287-16-44-C33-R65 | FN3288-16-44-C21-R65 | FN3288IT-16-44-C34-R65 | FN3120H-25-33 | FN3280H-16-29-69
6SL3210-1PE21-1AL0 | SINAMICS PM240-2 IP20-FSB-A-400V-4KW | FN3440-4-112-E2XXJRX | FN3450-6-112-E2XXJRX | FN3442-6-112-E2XXJRX | FN3452-5-112-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-8-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-9-88-E0XXX | RWK305-14-KL | RWK5420-13-89-E0XXT | FN5060-12-84 | FN5420-13-33-E2FXT | FN3440-4-112-E2XXJRX | FN3450-6-112-E2XXJRX | FN3442-6-112-E2XXJRX | FN3452-5-112-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-8-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-9-88-E0XXX | RWK305-14-KL | RWK5420-13-89-E0XXT | FN5060-12-84 | FN5420-13-33-E2FXT | FN3288-16-44-C35-R65 | FN3287-16-44-C33-R65 | FN3288-16-44-C21-R65 | FN3288IT-16-44-C34-R65 | FN3120H-25-33 | FN3280H-16-29-69
6SL3210-1PE21-4UL0 | SINAMICS PM240-2 IP20-FSB-U-400V-5.5KW | FN3440-6-112-E2XXJRX | FN3450-6-112-E2XXJRX | FN3442-6-112-E2XXJRX | FN3452-8-112-E2XXJRX | FN3446-6-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-10-44-E2XXJXX | FN3458-8-44-E2XXJXX | RWK3044-12-88-E0XXX | RWK305-17-KL | RWK5420-18-89-E0XXT | FN5060-24-84 | FN5420-18-33-E2FXT | FN3440-6-112-E2XXJRX | FN3450-6-112-E2XXJRX | FN3442-6-112-E2XXJRX | FN3452-8-112-E2XXJRX | FN3446-6-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-10-44-E2XXJXX | FN3458-8-44-E2XXJXX | RWK3044-12-88-E0XXX | RWK305-17-KL | RWK5420-18-89-E0XXT | FN5060-24-84 | FN5420-18-33-E2FXT | FN3288-20-33-C35-R65 | FN3287-20-33-C33-R65 | FN3288-20-33-C21-R65 | FN3288IT-20-33-C34-R65 | FN3120H-25-33 | FN3280H-25-33-69
6SL3210-1PE21-4AL0 | SINAMICS PM240-2 IP20-FSB-A-400V-5.5KW | FN3440-6-112-E2XXJRX | FN3450-6-112-E2XXJRX | FN3442-6-112-E2XXJRX | FN3452-8-112-E2XXJRX | FN3446-6-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-10-44-E2XXJXX | FN3458-8-44-E2XXJXX | RWK3044-12-88-E0XXX | RWK305-17-KL | RWK5420-18-89-E0XXT | FN5060-24-84 | FN5420-18-33-E2FXT | FN3440-6-112-E2XXJRX | FN3450-6-112-E2XXJRX | FN3442-6-112-E2XXJRX | FN3452-8-112-E2XXJRX | FN3446-6-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-10-44-E2XXJXX | FN3458-8-44-E2XXJXX | RWK3044-12-88-E0XXX | RWK305-17-KL | RWK5420-18-89-E0XXT | FN5060-24-84 | FN5420-18-33-E2FXT | FN3288-20-33-C35-R65 | FN3287-20-33-C33-R65 | FN3288-20-33-C21-R65 | FN3288IT-20-33-C34-R65 | FN3120H-25-33 | FN3280H-25-33-69
6SL3210-1PE21-8UL0 | SINAMICS PM240-2 IP20-FSB-U-400V-7.5KW | FN3440-8-112-E2XXJRX | FN3450-8-112-E2XXJRX | FN3442-12-112-E2XXJRX | FN3452-10-112-E2XXJRX | FN3446-8-44-E2XXJXX | FN3446-6-44-E2XXJXX | FN3458-15-33-E2FAJXX | FN3458-10-44-E2XXJXX | RWK3044-18-89-E0XXX | RWK305-24-KL | RWK5420-26-92-E0XXT | FN5060-24-84 | FN5420-26-33-E2FXT | FN3440-8-112-E2XXJRX | FN3450-8-112-E2XXJRX | FN3442-12-112-E2XXJRX | FN3452-10-112-E2XXJRX | FN3446-8-44-E2XXJXX | FN3446-6-44-E2XXJXX | FN3458-15-33-E2FAJXX | FN3458-10-44-E2XXJXX | RWK3044-18-89-E0XXX | RWK305-24-KL | RWK5420-26-92-E0XXT | FN5060-24-84 | FN5420-26-33-E2FXT | FN3288-25-33-C35-R65 | FN3287-25-33-C33-R65 | FN3288-25-33-C21-R65 | FN3288IT-25-33-C34-R65 | FN3120H-25-33 | FN3280H-25-33-69
6SL3211-1PE21-8UL0 | SINAMICS PM240-2 PT-FSB-U-400V-7.5KW | FN3440-8-112-E2XXJRX | FN3450-8-112-E2XXJRX | FN3442-12-112-E2XXJRX | FN3452-10-112-E2XXJRX | FN3446-8-44-E2XXJXX | FN3446-6-44-E2XXJXX | FN3458-15-33-E2FAJXX | FN3458-10-44-E2XXJXX | RWK3044-18-89-E0XXX | RWK305-24-KL | RWK5420-26-92-E0XXT | FN5060-24-84 | FN5420-26-33-E2FXT | FN3440-8-112-E2XXJRX | FN3450-8-112-E2XXJRX | FN3442-12-112-E2XXJRX | FN3452-10-112-E2XXJRX | FN3446-8-44-E2XXJXX | FN3446-6-44-E2XXJXX | FN3458-15-33-E2FAJXX | FN3458-10-44-E2XXJXX | RWK3044-18-89-E0XXX | RWK305-24-KL | RWK5420-26-92-E0XXT | FN5060-24-84 | FN5420-26-33-E2FXT | FN3288-25-33-C35-R65 | FN3287-25-33-C33-R65 | FN3288-25-33-C21-R65 | FN3288IT-25-33-C34-R65 | FN3120H-25-33 | FN3280H-25-33-69
6SL3210-1PE21-8AL0 | SINAMICS PM240-2 IP20-FSB-A-400V-7.5KW | FN3440-8-112-E2XXJRX | FN3450-8-112-E2XXJRX | FN3442-12-112-E2XXJRX | FN3452-10-112-E2XXJRX | FN3446-8-44-E2XXJXX | FN3446-6-44-E2XXJXX | FN3458-15-33-E2FAJXX | FN3458-10-44-E2XXJXX | RWK3044-18-89-E0XXX | RWK305-24-KL | RWK5420-26-92-E0XXT | FN5060-24-84 | FN5420-26-33-E2FXT | FN3440-8-112-E2XXJRX | FN3450-8-112-E2XXJRX | FN3442-12-112-E2XXJRX | FN3452-10-112-E2XXJRX | FN3446-8-44-E2XXJXX | FN3446-6-44-E2XXJXX | FN3458-15-33-E2FAJXX | FN3458-10-44-E2XXJXX | RWK3044-18-89-E0XXX | RWK305-24-KL | RWK5420-26-92-E0XXT | FN5060-24-84 | FN5420-26-33-E2FXT | FN3288-25-33-C35-R65 | FN3287-25-33-C33-R65 | FN3288-25-33-C21-R65 | FN3288IT-25-33-C34-R65 | FN3120H-25-33 | FN3280H-25-33-69
6SL3211-1PE21-8AL0 | SINAMICS PM240-2 PT-FSB-A-400V-7.5KW | FN3440-8-112-E2XXJRX | FN3450-8-112-E2XXJRX | FN3442-12-112-E2XXJRX | FN3452-10-112-E2XXJRX | FN3446-8-44-E2XXJXX | FN3446-6-44-E2XXJXX | FN3458-15-33-E2FAJXX | FN3458-10-44-E2XXJXX | RWK3044-18-89-E0XXX | RWK305-24-KL | RWK5420-26-92-E0XXT | FN5060-24-84 | FN5420-26-33-E2FXT | FN3440-8-112-E2XXJRX | FN3450-8-112-E2XXJRX | FN3442-12-112-E2XXJRX | FN3452-10-112-E2XXJRX | FN3446-8-44-E2XXJXX | FN3446-6-44-E2XXJXX | FN3458-15-33-E2FAJXX | FN3458-10-44-E2XXJXX | RWK3044-18-89-E0XXX | RWK305-24-KL | RWK5420-26-92-E0XXT | FN5060-24-84 | FN5420-26-33-E2FXT | FN3288-25-33-C35-R65 | FN3287-25-33-C33-R65 | FN3288-25-33-C21-R65 | FN3288IT-25-33-C34-R65 | FN3120H-25-33 | FN3280H-25-33-69
6SL3210-1PE22-7UL0 | SINAMICS PM240-2 IP20-FSC-U-400V-11KW | FN3440-11-113-E2FAJRX | FN3450-15-113-E2FAJRX | FN3442-16-113-E2FAJRX | FN3452-15-112-E2XXJRX | FN3446-11-33-E2FAJXX | FN3446-11-33-E2FAJXX | FN3458-20-33-E2FAJXX | FN3458-15-33-E2FAJXX | RWK3044-24-89-E0XXX | RWK305-32-KL | RWK5420-32-92-E0XXT | FN5060-30-99 | FN5420-32-33-E2FXT | FN3440-11-113-E2FAJRX | FN3450-15-113-E2FAJRX | FN3442-12-112-E2XXJRX | FN3452-15-112-E2XXJRX | FN3446-11-33-E2FAJXX | FN3446-8-44-E2XXJXX | FN3458-15-33-E2FAJXX | FN3458-15-33-E2FAJXX | RWK3044-24-89-E0XXX | RWK305-32-KL | RWK5420-32-92-E0XXT | FN5060-30-99 | FN5420-32-33-E2FXT | FN3288-40-33-C35-R65 | FN3287-40-33-C33-R65 | FN3288-40-33-C21-R65 | FN3288IT-40-33-C34-R65 | FN3120H-50-53 | FN3280H-36-33-69
6SL3210-1PE22-7AL0 | SINAMICS PM240-2 IP20-FSC-A-400V-11KW | FN3440-11-113-E2FAJRX | FN3450-15-113-E2FAJRX | FN3442-16-113-E2FAJRX | FN3452-15-112-E2XXJRX | FN3446-11-33-E2FAJXX | FN3446-11-33-E2FAJXX | FN3458-20-33-E2FAJXX | FN3458-15-33-E2FAJXX | RWK3044-24-89-E0XXX | RWK305-32-KL | RWK5420-32-92-E0XXT | FN5060-30-99 | FN5420-32-33-E2FXT | FN3440-11-113-E2FAJRX | FN3450-15-113-E2FAJRX | FN3442-12-112-E2XXJRX | FN3452-15-112-E2XXJRX | FN3446-11-33-E2FAJXX | FN3446-8-44-E2XXJXX | FN3458-15-33-E2FAJXX | FN3458-15-33-E2FAJXX | RWK3044-24-89-E0XXX | RWK305-32-KL | RWK5420-32-92-E0XXT | FN5060-30-99 | FN5420-32-33-E2FXT | FN3288-40-33-C35-R65 | FN3287-40-33-C33-R65 | FN3288-40-33-C21-R65 | FN3288IT-40-33-C34-R65 | FN3120H-50-53 | FN3280H-36-33-69
6SL3210-1PE23-3UL0 | SINAMICS PM240-2 IP20-FSC-U-400V-15KW | FN3440-15-113-E2FAJRX | FN3450-19-113-E2FAJRX | FN3442-20-113-E2FAJRX | FN3452-20-113-E2FAJRX | FN3446-15-33-E2FAJXX | FN3446-11-33-E2FAJXX | FN3458-25-33-E2FAJXX | FN3458-20-33-E2FAJXX | RWK3044-30-92-E0XXX | RWK305-45-KL | RWK5420-38-92-E0XXT | FN5060-45-99 | FN5420-38-33-E2FXT | FN3440-15-113-E2FAJRX | FN3450-19-113-E2FAJRX | FN3442-20-113-E2FAJRX | FN3452-20-113-E2FAJRX | FN3446-15-33-E2FAJXX | FN3446-11-33-E2FAJXX | FN3458-25-33-E2FAJXX | FN3458-20-33-E2FAJXX | RWK3044-30-92-E0XXX | RWK305-45-KL | RWK5420-45-92-E0XXT | FN5060-45-99 | FN5420-45-34-E2FXT | FN3288-40-33-C35-R65 | FN3287-40-33-C33-R65 | FN3288-40-33-C21-R65 | FN3288IT-40-33-C34-R65 | FN3120H-50-53 | FN3280H-64-34-69
6SL3211-1PE23-3UL0 | SINAMICS PM240-2 PT-FSC-U-400V-15KW | FN3440-15-113-E2FAJRX | FN3450-19-113-E2FAJRX | FN3442-20-113-E2FAJRX | FN3452-20-113-E2FAJRX | FN3446-15-33-E2FAJXX | FN3446-11-33-E2FAJXX | FN3458-25-33-E2FAJXX | FN3458-20-33-E2FAJXX | RWK3044-30-92-E0XXX | RWK305-45-KL | RWK5420-38-92-E0XXT | FN5060-45-99 | FN5420-38-33-E2FXT | FN3440-15-113-E2FAJRX | FN3450-19-113-E2FAJRX | FN3442-20-113-E2FAJRX | FN3452-20-113-E2FAJRX | FN3446-15-33-E2FAJXX | FN3446-11-33-E2FAJXX | FN3458-25-33-E2FAJXX | FN3458-20-33-E2FAJXX | RWK3044-30-92-E0XXX | RWK305-45-KL | RWK5420-45-92-E0XXT | FN5060-45-99 | FN5420-45-34-E2FXT | FN3288-40-33-C35-R65 | FN3287-40-33-C33-R65 | FN3288-40-33-C21-R65 | FN3288IT-40-33-C34-R65 | FN3120H-50-53 | FN3280H-64-34-69
6SL3210-1PE23-3AL0 | SINAMICS PM240-2 IP20-FSC-A-400V-15KW | FN3440-15-113-E2FAJRX | FN3450-19-113-E2FAJRX | FN3442-20-113-E2FAJRX | FN3452-20-113-E2FAJRX | FN3446-15-33-E2FAJXX | FN3446-11-33-E2FAJXX | FN3458-25-33-E2FAJXX | FN3458-20-33-E2FAJXX | RWK3044-30-92-E0XXX | RWK305-45-KL | RWK5420-38-92-E0XXT | FN5060-45-99 | FN5420-38-33-E2FXT | FN3440-15-113-E2FAJRX | FN3450-19-113-E2FAJRX | FN3442-20-113-E2FAJRX | FN3452-20-113-E2FAJRX | FN3446-15-33-E2FAJXX | FN3446-11-33-E2FAJXX | FN3458-25-33-E2FAJXX | FN3458-20-33-E2FAJXX | RWK3044-30-92-E0XXX | RWK305-45-KL | RWK5420-45-92-E0XXT | FN5060-45-99 | FN5420-45-34-E2FXT | FN3288-40-33-C35-R65 | FN3287-40-33-C33-R65 | FN3288-40-33-C21-R65 | FN3288IT-40-33-C34-R65 | FN3120H-50-53 | FN3280H-64-34-69
6SL3211-1PE23-3AL0 | SINAMICS PM240-2 PT-FSC-A-400V-15KW | FN3440-15-113-E2FAJRX | FN3450-19-113-E2FAJRX | FN3442-20-113-E2FAJRX | FN3452-20-113-E2FAJRX | FN3446-15-33-E2FAJXX | FN3446-11-33-E2FAJXX | FN3458-25-33-E2FAJXX | FN3458-20-33-E2FAJXX | RWK3044-30-92-E0XXX | RWK305-45-KL | RWK5420-38-92-E0XXT | FN5060-45-99 | FN5420-38-33-E2FXT | FN3440-15-113-E2FAJRX | FN3450-19-113-E2FAJRX | FN3442-20-113-E2FAJRX | FN3452-20-113-E2FAJRX | FN3446-15-33-E2FAJXX | FN3446-11-33-E2FAJXX | FN3458-25-33-E2FAJXX | FN3458-20-33-E2FAJXX | RWK3044-30-92-E0XXX | RWK305-45-KL | RWK5420-45-92-E0XXT | FN5060-45-99 | FN5420-45-34-E2FXT | FN3288-40-33-C35-R65 | FN3287-40-33-C33-R65 | FN3288-40-33-C21-R65 | FN3288IT-40-33-C34-R65 | FN3120H-50-53 | FN3280H-64-34-69
6SL3210-1PE23-8UL0 | SINAMICS PM240-2 IP20-FSD-U-400V-18.5kW | FN3440-19-113-E2FAJRX | FN3450-19-113-E2FAJRX | FN3442-24-113-E2FAJRX | FN3452-25-113-E2FAJRX | FN3446-19-33-E2FAJXX | FN3446-15-33-E2FAJXX | FN3458-30-33-E2FAJXX | FN3458-25-33-E2FAJXX | RWK3044-48-92-E0XXX | RWK305-45-KL | RWK5420-45-92-E0XXT | FN5060-45-99 | FN5420-45-34-E2FXT | FN3440-22-115-E2FAJRX | FN3450-22-113-E2FAJRX | FN3442-24-113-E2FAJRX | FN3452-25-113-E2FAJRX | FN3446-19-33-E2FAJXX | FN3446-19-33-E2FAJXX | FN3458-30-33-E2FAJXX | FN3458-25-33-E2FAJXX | RWK3044-48-92-E0XXX | RWK305-60-KL | RWK5420-60-92-E0XXT | FN5060-60-99 | FN5420-60-34-E2FXT | FN3288-40-33-C35-R65 | FN3287-40-33-C33-R65 | FN3288-40-33-C21-R65 | FN3288IT-40-33-C34-R65 | FN3120H-50-53 | FN3280H-64-34-69
6SL3210-1PE23-8AL0 | SINAMICS PM240-2 IP20-FSD-A-400V-18.5kW | FN3440-19-113-E2FAJRX | FN3450-19-113-E2FAJRX | FN3442-24-113-E2FAJRX | FN3452-25-113-E2FAJRX | FN3446-19-33-E2FAJXX | FN3446-15-33-E2FAJXX | FN3458-30-33-E2FAJXX | FN3458-25-33-E2FAJXX | RWK3044-48-92-E0XXX | RWK305-45-KL | RWK5420-45-92-E0XXT | FN5060-45-99 | FN5420-45-34-E2FXT | FN3440-22-115-E2FAJRX | FN3450-22-113-E2FAJRX | FN3442-24-113-E2FAJRX | FN3452-25-113-E2FAJRX | FN3446-19-33-E2FAJXX | FN3446-19-33-E2FAJXX | FN3458-30-33-E2FAJXX | FN3458-25-33-E2FAJXX | RWK3044-48-92-E0XXX | RWK305-60-KL | RWK5420-60-92-E0XXT | FN5060-60-99 | FN5420-60-34-E2FXT | FN3288-40-33-C35-R65 | FN3287-40-33-C33-R65 | FN3288-40-33-C21-R65 | FN3288IT-40-33-C34-R65 | FN3120H-50-53 | FN3280H-64-34-69
6SL3210-1PE24-5UL0 | SINAMICS PM240-2 IP20-FSD-U-400V-22kW | FN3440-22-115-E2FAJRX | FN3450-22-113-E2FAJRX | FN3442-24-113-E2FAJRX | FN3452-30-113-E2FAJRX | FN3446-22-33-E2FAJXX | FN3446-19-33-E2FAJXX | FN3458-40-34-E2FAJXX | FN3458-30-33-E2FAJXX | RWK3044-48-92-E0XXX | RWK305-60-KL | RWK5420-60-92-E0XXT | FN5060-60-99 | FN5420-60-34-E2FXT | FN3440-30-115-E2FAJRX | FN3450-30-115-E2FAJRX | FN3442-32-115-E2FAJRX | FN3452-30-113-E2FAJRX | FN3446-22-33-E2FAJXX | FN3446-19-33-E2FAJXX | FN3458-40-34-E2FAJXX | FN3458-30-33-E2FAJXX | RWK3044-59-92-E0XXX | RWK305-60-KL | RWK5420-60-92-E0XXT | FN5060-60-99 | FN5420-60-34-E2FXT | FN3288-50-53-C35-R65 | FN3287-50-53-C33-R65 | FN3288-50-53-C21-R65 | FN3288IT-50-53-C34-R65 | FN3120H-50-53 | FN3280H-64-34-69
6SL3210-1PE24-5AL0 | SINAMICS PM240-2 IP20-FSD-A-400V-22kW | FN3440-22-115-E2FAJRX | FN3450-22-113-E2FAJRX | FN3442-24-113-E2FAJRX | FN3452-30-113-E2FAJRX | FN3446-22-33-E2FAJXX | FN3446-19-33-E2FAJXX | FN3458-40-34-E2FAJXX | FN3458-30-33-E2FAJXX | RWK3044-48-92-E0XXX | RWK305-60-KL | RWK5420-60-92-E0XXT | FN5060-60-99 | FN5420-60-34-E2FXT | FN3440-30-115-E2FAJRX | FN3450-30-115-E2FAJRX | FN3442-32-115-E2FAJRX | FN3452-30-113-E2FAJRX | FN3446-22-33-E2FAJXX | FN3446-19-33-E2FAJXX | FN3458-40-34-E2FAJXX | FN3458-30-33-E2FAJXX | RWK3044-59-92-E0XXX | RWK305-60-KL | RWK5420-60-92-E0XXT | FN5060-60-99 | FN5420-60-34-E2FXT | FN3288-50-53-C35-R65 | FN3287-50-53-C33-R65 | FN3288-50-53-C21-R65 | FN3288IT-50-53-C34-R65 | FN3120H-50-53 | FN3280H-64-34-69
6SL3210-1PE26-0UL0 | SINAMICS PM240-2 IP20-FSD-U-400V-30kW | FN3440-30-115-E2FAJRX | FN3450-37-115-E2FAJRX | FN3442-40-115-E2FAJRX | FN3452-40-115-E2FAJRX | FN3446-30-34-E2FAJXX | FN3446-22-33-E2FAJXX | FN3458-50-34-E2FAJXX | FN3458-40-34-E2FAJXX | RWK3044-59-92-E0XXX | RWK305-72-KL | RWK5420-75-99-E0XXT | FN5060-70-99 | FN5420-75-35-E2FXT | FN3440-30-115-E2FAJRX | FN3450-37-115-E2FAJRX | FN3442-40-115-E2FAJRX | FN3452-40-115-E2FAJRX | FN3446-30-34-E2FAJXX | FN3446-22-33-E2FAJXX | FN3458-50-34-E2FAJXX | FN3458-40-34-E2FAJXX | RWK3044-59-92-E0XXX | RWK305-72-KL | RWK5420-75-99-E0XXT | FN5060-70-99 | FN5420-75-35-E2FXT | FN3288-63-53-C35-R65 | FN3287-63-53-C33-R65 | FN3288-63-53-C21-R65 | FN3288IT-63-53-C34-R65 | FN3120H-80-35 | FN3280H-64-34-69
6SL3210-1PE26-0AL0 | SINAMICS PM240-2 IP20-FSD-A-400V-30kW | FN3440-30-115-E2FAJRX | FN3450-37-115-E2FAJRX | FN3442-40-115-E2FAJRX | FN3452-40-115-E2FAJRX | FN3446-30-34-E2FAJXX | FN3446-22-33-E2FAJXX | FN3458-50-34-E2FAJXX | FN3458-40-34-E2FAJXX | RWK3044-59-92-E0XXX | RWK305-72-KL | RWK5420-75-99-E0XXT | FN5060-70-99 | FN5420-75-35-E2FXT | FN3440-30-115-E2FAJRX | FN3450-37-115-E2FAJRX | FN3442-40-115-E2FAJRX | FN3452-40-115-E2FAJRX | FN3446-30-34-E2FAJXX | FN3446-22-33-E2FAJXX | FN3458-50-34-E2FAJXX | FN3458-40-34-E2FAJXX | RWK3044-59-92-E0XXX | RWK305-72-KL | RWK5420-75-99-E0XXT | FN5060-70-99 | FN5420-75-35-E2FXT | FN3288-63-53-C35-R65 | FN3287-63-53-C33-R65 | FN3288-63-53-C21-R65 | FN3288IT-63-53-C34-R65 | FN3120H-80-35 | FN3280H-64-34-69
6SL3210-1PE27-5UL0 | SINAMICS PM240-2 IP20-FSD-U-400V-37kW | FN3440-37-115-E2FAJRX | FN3450-45-115-E2FAJRX | FN3442-48-115-E2FAJRX | FN3452-50-115-E2FAJRX | FN3446-37-34-E2FAJXX | FN3446-30-34-E2FAJXX | FN3458-60-35-E2FAJXX | FN3458-50-34-E2FAJXX | RWK3044-72-99-E0XXX | RWK305-90-KL | RWK5420-90-99-E0XXT | FN5060-90-99 | FN5420-90-35-E2FXT | FN3440-45-115-E2FAJRX | FN3450-45-115-E2FAJRX | FN3442-48-115-E2FAJRX | FN3452-60-115-E2FAJRX | FN3446-37-34-E2FAJXX | FN3446-30-34-E2FAJXX | FN3458-60-35-E2FAJXX | FN3458-50-34-E2FAJXX | RWK3044-88-99-E0XXX | RWK305-90-KL | RWK5420-90-99-E0XXT | FN5060-90-99 | FN5420-90-35-E2FXT | FN3288-80-34-C35-R65 | FN3287-80-34-C33-R65 | FN3288-80-34-C21-R65 | FN3288IT-80-34-C34-R65 | FN3120H-80-35 | FN3280H-80-35-69
6SL3210-1PE27-5AL0 | SINAMICS PM240-2 IP20-FSD-A-400V-37kW | FN3440-37-115-E2FAJRX | FN3450-45-115-E2FAJRX | FN3442-48-115-E2FAJRX | FN3452-50-115-E2FAJRX | FN3446-37-34-E2FAJXX | FN3446-30-34-E2FAJXX | FN3458-60-35-E2FAJXX | FN3458-50-34-E2FAJXX | RWK3044-72-99-E0XXX | RWK305-90-KL | RWK5420-90-99-E0XXT | FN5060-90-99 | FN5420-90-35-E2FXT | FN3440-45-115-E2FAJRX | FN3450-45-115-E2FAJRX | FN3442-48-115-E2FAJRX | FN3452-60-115-E2FAJRX | FN3446-37-34-E2FAJXX | FN3446-30-34-E2FAJXX | FN3458-60-35-E2FAJXX | FN3458-50-34-E2FAJXX | RWK3044-88-99-E0XXX | RWK305-90-KL | RWK5420-90-99-E0XXT | FN5060-90-99 | FN5420-90-35-E2FXT | FN3288-80-34-C35-R65 | FN3287-80-34-C33-R65 | FN3288-80-34-C21-R65 | FN3288IT-80-34-C34-R65 | FN3120H-80-35 | FN3280H-80-35-69
6SL3210-1PE28-8UL0 | SINAMICS PM240-2 IP20-FSE-U-400V-45kW | FN3440-45-115-E2FAJRX | FN3450-45-115-E2FAJRX | FN3442-60-115-E2FAJRX | FN3452-60-115-E2FAJRX | FN3446-45-35-E2FAJXX | FN3446-37-34-E2FAJXX | FN3458-75-35-E2FAJXX | FN3458-60-35-E2FAJXX | RWK3044-88-99-E0XXX | RWK305-110-KL | RWK5420-110-99-E0XXT | FN5060-110-99 | FN5420-110-35-E2FXT | FN3440-55-115-E2FAJRX | FN3450-55-115-E2FAJRX | FN3442-60-115-E2FAJRX | FN3452-60-115-E2FAJRX | FN3446-45-35-E2FAJXX | FN3446-45-35-E2FAJXX | FN3458-75-35-E2FAJXX | FN3458-75-35-E2FAJXX | RWK3044-120-99-E0XXX | RWK305-124-KS | RWK5420-145-99-E0XXT | FN5060-150-99 | FN5420-145-99-E0XXT | FN3288-100-35-C35-R65 | FN3287-100-35-C33-R65 | FN3288-100-35-C21-R65 | FN3288IT-100-35-C34-R65 | FN3120H-110-35 | FN3280H-120-35-69
6SL3210-1PE28-8AL0 | SINAMICS PM240-2 IP20-FSE-A-400V-45kW | FN3440-45-115-E2FAJRX | FN3450-45-115-E2FAJRX | FN3442-60-115-E2FAJRX | FN3452-60-115-E2FAJRX | FN3446-45-35-E2FAJXX | FN3446-37-34-E2FAJXX | FN3458-75-35-E2FAJXX | FN3458-60-35-E2FAJXX | RWK3044-88-99-E0XXX | RWK305-110-KL | RWK5420-110-99-E0XXT | FN5060-110-99 | FN5420-110-35-E2FXT | FN3440-55-115-E2FAJRX | FN3450-55-115-E2FAJRX | FN3442-60-115-E2FAJRX | FN3452-60-115-E2FAJRX | FN3446-45-35-E2FAJXX | FN3446-45-35-E2FAJXX | FN3458-75-35-E2FAJXX | FN3458-75-35-E2FAJXX | RWK3044-120-99-E0XXX | RWK305-124-KS | RWK5420-145-99-E0XXT | FN5060-150-99 | FN5420-145-99-E0XXT | FN3288-100-35-C35-R65 | FN3287-100-35-C33-R65 | FN3288-100-35-C21-R65 | FN3288IT-100-35-C34-R65 | FN3120H-110-35 | FN3280H-120-35-69
6SL3210-1PE31-1UL0 | SINAMICS PM240-2 IP20-FSE-U-400V-55kW | FN3440-55-115-E2FAJRX | FN3450-55-115-E2FAJRX | FN3442-80-115-E2FAJRX | FN3452-75-115-E2FAJRX | FN3446-55-35-E2FAJXX | FN3446-45-35-E2FAJXX | FN3458-100-40-E2FAJXX | FN3458-75-35-E2FAJXX | RWK3044-120-99-E0XXX | RWK305-124-KS | RWK5420-145-99-E0XXT | FN5060-150-99 | FN5420-145-99-E0XXT | FN3440-75-116-E2FAJRX | FN3450-75-115-E2FAJRX | FN3442-80-115-E2FAJRX | FN3452-75-115-E2FAJRX | FN3446-55-35-E2FAJXX | FN3446-55-35-E2FAJXX | FN3458-100-40-E2FAJXX | FN3458-100-40-E2FAJXX | RWK3044-120-99-E0XXX | RWK305-143-KS | RWK5420-145-99-E0XXT | FN5060-150-99 | FN5420-145-99-E0XXT | FN3288-125-35-C35-R65 | FN3287-125-35-C33-R65 | FN3288-125-35-C21-R65 | FN3288IT-125-35-C34-R65 | FN3120H-110-35 | FN3280H-120-35-69
6SL3210-1PE31-1AL0 | SINAMICS PM240-2 IP20-FSE-A-400V-55kW | FN3440-55-115-E2FAJRX | FN3450-55-115-E2FAJRX | FN3442-80-115-E2FAJRX | FN3452-75-115-E2FAJRX | FN3446-55-35-E2FAJXX | FN3446-45-35-E2FAJXX | FN3458-100-40-E2FAJXX | FN3458-75-35-E2FAJXX | RWK3044-120-99-E0XXX | RWK305-124-KS | RWK5420-145-99-E0XXT | FN5060-150-99 | FN5420-145-99-E0XXT | FN3440-75-116-E2FAJRX | FN3450-75-115-E2FAJRX | FN3442-80-115-E2FAJRX | FN3452-75-115-E2FAJRX | FN3446-55-35-E2FAJXX | FN3446-55-35-E2FAJXX | FN3458-100-40-E2FAJXX | FN3458-100-40-E2FAJXX | RWK3044-120-99-E0XXX | RWK305-143-KS | RWK5420-145-99-E0XXT | FN5060-150-99 | FN5420-145-99-E0XXT | FN3288-125-35-C35-R65 | FN3287-125-35-C33-R65 | FN3288-125-35-C21-R65 | FN3288IT-125-35-C34-R65 | FN3120H-110-35 | FN3280H-120-35-69
6SL3210-1PE31-5UL0 | SINAMICS PM240-2 IP20-FSF-U-400V-75kW | FN3440-75-116-E2FAJRX | FN3450-90-116-E2FAJRX | FN3442-100-116-E2FAJRX | FN3452-100-115-E2FAJRX | FN3446-75-40-E2FAJXX | FN3446-75-40-E2FAJXX | FN3458-125-40-E2FAJXX | FN3458-100-40-E2FAJXX | RWK3044-180-99-E0XXX | RWK305-170-KS | RWK5420-180-99-E0XXT | FN5060-180-99 | FN5420-180-99-E0XXT | FN3440-75-116-E2FAJRX | FN3450-90-116-E2FAJRX | FN3442-100-116-E2FAJRX | FN3452-100-115-E2FAJRX | FN3446-75-40-E2FAJXX | FN3446-75-40-E2FAJXX | FN3458-125-40-E2FAJXX | FN3458-100-40-E2FAJXX | RWK3044-180-99-E0XXX | RWK305-170-KS | RWK5420-180-99-E0XXT | FN5060-180-99 | FN5420-180-99-E0XXT | FN3288-160-40-C35-R65 | FN3287-160-40-C33-R65 | FN3288-160-40-C21-R65 | FN3288IT-160-40-C34-R65 | FN3120H-150-40 | FN3280H-160-40-69
6SL3210-1PE31-5AL0 | SINAMICS PM240-2 IP20-FSF-A-400V-75kW | FN3440-75-116-E2FAJRX | FN3450-90-116-E2FAJRX | FN3442-100-116-E2FAJRX | FN3452-100-115-E2FAJRX | FN3446-75-40-E2FAJXX | FN3446-75-40-E2FAJXX | FN3458-125-40-E2FAJXX | FN3458-100-40-E2FAJXX | RWK3044-180-99-E0XXX | RWK305-170-KS | RWK5420-180-99-E0XXT | FN5060-180-99 | FN5420-180-99-E0XXT | FN3440-75-116-E2FAJRX | FN3450-90-116-E2FAJRX | FN3442-100-116-E2FAJRX | FN3452-100-115-E2FAJRX | FN3446-75-40-E2FAJXX | FN3446-75-40-E2FAJXX | FN3458-125-40-E2FAJXX | FN3458-100-40-E2FAJXX | RWK3044-180-99-E0XXX | RWK305-170-KS | RWK5420-180-99-E0XXT | FN5060-180-99 | FN5420-180-99-E0XXT | FN3288-160-40-C35-R65 | FN3287-160-40-C33-R65 | FN3288-160-40-C21-R65 | FN3288IT-160-40-C34-R65 | FN3120H-150-40 | FN3280H-160-40-69
6SL3210-1PE31-8UL0 | SINAMICS PM240-2 IP20-FSF-U-400V-90kW | FN3440-90-116-E2FAJRX | FN3450-90-116-E2FAJRX | FN3442-120-116-E2FAJRX | FN3452-125-116-E2FAJRX | FN3446-90-40-E2FAJXX | FN3446-75-40-E2FAJXX | FN3458-150-40-E2FAJXX | FN3458-125-40-E2FAJXX | RWK3044-180-99-E0XXX | RWK305-230-KS | RWK5420-200-99-E0XXT | FN5060-250-99 | FN5420-200-99-E0XXT | FN3440-110-118-E2FAJRX | FN3450-110-116-E2FAJRX | FN3442-120-116-E2FAJRX | FN3452-150-116-E2FAJRX | FN3446-110-40-E2FAJXX | FN3446-90-40-E2FAJXX | FN3458-200-99-E2FAJXX | FN3458-150-40-E2FAJXX | RWK3044-210-99-E0XXX | RWK305-230-KS | RWK5420-250-99-E0XXT | FN5060-250-99 | FN5420-250-99-E0XXT | FN3288-230-40-C35-R65 | FN3287-230-40-C33-R65 | FN3288-230-40-C21-R65 | FN3288IT-230-40-C34-R65 | FN3120H-230-40 | FN3280H-200-40-69
6SL3210-1PE31-8AL0 | SINAMICS PM240-2 IP20-FSF-A-400V-90kW | FN3440-90-116-E2FAJRX | FN3450-90-116-E2FAJRX | FN3442-120-116-E2FAJRX | FN3452-125-116-E2FAJRX | FN3446-90-40-E2FAJXX | FN3446-75-40-E2FAJXX | FN3458-150-40-E2FAJXX | FN3458-125-40-E2FAJXX | RWK3044-180-99-E0XXX | RWK305-230-KS | RWK5420-200-99-E0XXT | FN5060-250-99 | FN5420-200-99-E0XXT | FN3440-110-118-E2FAJRX | FN3450-110-116-E2FAJRX | FN3442-120-116-E2FAJRX | FN3452-150-116-E2FAJRX | FN3446-110-40-E2FAJXX | FN3446-90-40-E2FAJXX | FN3458-200-99-E2FAJXX | FN3458-150-40-E2FAJXX | RWK3044-210-99-E0XXX | RWK305-230-KS | RWK5420-250-99-E0XXT | FN5060-250-99 | FN5420-250-99-E0XXT | FN3288-230-40-C35-R65 | FN3287-230-40-C33-R65 | FN3288-230-40-C21-R65 | FN3288IT-230-40-C34-R65 | FN3120H-230-40 | FN3280H-200-40-69
6SL3210-1PE32-1UL0 | SINAMICS PM240-2 IP20-FSF-U-400V-110kW | FN3440-132-118-E2FAJXX | FN3450-110-116-E2FAJRX | FN3442-160-118-E2FAJRX | FN3452-150-116-E2FAJRX | FN3446-110-40-E2FAJXX | FN3446-90-40-E2FAJXX | FN3458-200-99-E2FAJXX | FN3458-150-40-E2FAJXX | RWK3044-260-99-E0XXX | RWK305-230-KS | RWK5420-250-99-E0XXT | FN5060-250-99 | FN5420-250-99-E0XXT | FN3440-132-118-E2FAJXX | FN3450-132-118-E2FAJRX | FN3442-160-118-E2FAJRX | FN3452-150-116-E2FAJRX | FN3446-132-99-E2FAJXX | FN3446-110-40-E2FAJXX | FN3458-200-99-E2FAJXX | FN3458-200-99-E2FAJXX | RWK3044-260-99-E0XXX | RWK305-280-KS | RWK5420-300-99-E0XXT | FN5060-320-99 | FN5420-300-99-E0XXT | FN3288-230-40-C35-R65 | FN3287-230-40-C33-R65 | FN3288-230-40-C21-R65 | FN3288IT-230-40-C34-R65 | FN3120H-230-40 | FN3280H-200-40-69
6SL3210-1PE32-1AL0 | SINAMICS PM240-2 IP20-FSF-A-400V-110kW | FN3440-132-118-E2FAJXX | FN3450-110-116-E2FAJRX | FN3442-160-118-E2FAJRX | FN3452-150-116-E2FAJRX | FN3446-110-40-E2FAJXX | FN3446-90-40-E2FAJXX | FN3458-200-99-E2FAJXX | FN3458-150-40-E2FAJXX | RWK3044-260-99-E0XXX | RWK305-230-KS | RWK5420-250-99-E0XXT | FN5060-250-99 | FN5420-250-99-E0XXT | FN3440-132-118-E2FAJXX | FN3450-132-118-E2FAJRX | FN3442-160-118-E2FAJRX | FN3452-150-116-E2FAJRX | FN3446-132-99-E2FAJXX | FN3446-110-40-E2FAJXX | FN3458-200-99-E2FAJXX | FN3458-200-99-E2FAJXX | RWK3044-260-99-E0XXX | RWK305-280-KS | RWK5420-300-99-E0XXT | FN5060-320-99 | FN5420-300-99-E0XXT | FN3288-230-40-C35-R65 | FN3287-230-40-C33-R65 | FN3288-230-40-C21-R65 | FN3288IT-230-40-C34-R65 | FN3120H-230-40 | FN3280H-200-40-69
6SL3210-1PE32-5UL0 | SINAMICS PM240-2 IP20-FSF-U-400V-132kW | FN3440-132-118-E2FAJXX | FN3450-160-118-E2FAJXX | FN3442-200-118-E2FAJXX | FN3452-200-118-E2FAJRX | FN3446-132-99-E2FAJXX | FN3446-110-40-E2FAJXX | FN3458-250-99-E2FAJXX | FN3458-200-99-E2FAJXX | RWK3044-320-99-E0XXX | RWK305-280-KS | RWK5420-300-99-E0XXT | FN5060-320-99 | FN5420-300-99-E0XXT | FN3440-160-118-E2FAJXX | FN3450-160-118-E2FAJXX | FN3442-200-118-E2FAJXX | FN3452-250-118-E2FAJXX | FN3446-160-99-E2FAJXX | FN3446-132-99-E2FAJXX | FN3458-250-99-E2FAJXX | FN3458-200-99-E2FAJXX | RWK3044-320-99-E0XXX | RWK305-330-KS | RWK5420-300-99-E0XXT | FN5060-320-99 | FN5420-300-99-E0XXT | FN3359-250-28 | FN3270H-250-99 |  | FN3359HV-250-28 |  | FN3280H-300-99-69
6SL3210-1PE32-5AL0 | SINAMICS PM240-2 IP20-FSF-A-400V-132kW | FN3440-132-118-E2FAJXX | FN3450-160-118-E2FAJXX | FN3442-200-118-E2FAJXX | FN3452-200-118-E2FAJRX | FN3446-132-99-E2FAJXX | FN3446-110-40-E2FAJXX | FN3458-250-99-E2FAJXX | FN3458-200-99-E2FAJXX | RWK3044-320-99-E0XXX | RWK305-280-KS | RWK5420-300-99-E0XXT | FN5060-320-99 | FN5420-300-99-E0XXT | FN3440-160-118-E2FAJXX | FN3450-160-118-E2FAJXX | FN3442-200-118-E2FAJXX | FN3452-250-118-E2FAJXX | FN3446-160-99-E2FAJXX | FN3446-132-99-E2FAJXX | FN3458-250-99-E2FAJXX | FN3458-200-99-E2FAJXX | RWK3044-320-99-E0XXX | RWK305-330-KS | RWK5420-300-99-E0XXT | FN5060-320-99 | FN5420-300-99-E0XXT | FN3359-250-28 | FN3270H-250-99 |  | FN3359HV-250-28 |  | FN3280H-300-99-69
6SL3224-0XE41-3UA0 | SINAMICS PM240-IP20-FSGX-U-400V 132.0KW | FN3440-160-118-E2FAJXX | FN3450-160-118-E2FAJXX | FN3442-200-118-E2FAJXX | FN3452-250-118-E2FAJXX | FN3446-160-99-E2FAJXX | FN3446-132-99-E2FAJXX | FN3458-300-99-E2FAJXX | FN3458-250-99-E2FAJXX | RWK3044-320-99-E0XXX | RWK305-330-KS | RWK5420-400-99-E0XXT | FN5060-400-99 | FN5420-400-99-E0XXT | FN3440-200-118-E2FAJXX | FN3450-200-118-E2FAJXX | FN3442-240-118-E2FAJXX | FN3452-250-118-E2FAJXX | FN3446-200-99-E2FAJXX | FN3446-160-99-E2FAJXX | FN3458-300-99-E2FAJXX | FN3458-250-99-E2FAJXX | RWK3044-400-99-E0XXX | RWK305-400-S | RWK5420-400-99-E0XXT | FN5060-400-99 | FN5420-400-99-E0XXT | FN3359-320-99 | FN3270H-320-99 |  | FN3359HV-320-99 |  | FN3280H-300-99-69
6SL3224-0XE41-6UA0 | SINAMICS PM240-IP20-FSGX-U-400V 160.0KW | FN3440-200-118-E2FAJXX | FN3450-250-118-E2FAJXX | FN3442-240-118-E2FAJXX | FN3452-300-118-E2FAJXX | FN3446-200-99-E2FAJXX | FN3446-160-99-E2FAJXX | FN3473-280-99-E0XXJXX | FN3458-300-99-E2FAJXX | RWK3044-400-99-E0XXX | RWK305-400-S | RWK5420-400-99-E0XXT | FN5060-400-99 | FN5420-400-99-E0XXT | FN3440-250-119-E2FASXX | FN3450-250-118-E2FAJXX | FN3472-280-99-E0XXJXX | FN3452-300-118-E2FAJXX | FN3471-250-99-E0XXJXX | FN3446-200-99-E2FAJXX | FN3473-280-99-E0XXJXX | FN3458-300-99-E2FAJXX | RWK3044-510-99-E0XXX | RWK305-500-S | RWK5420-480-99-E0XXT | FN5060-500-99 | FN5420-480-99-E0XXT | FN3359-400-99 | FN3270H-400-99 |  | FN3359HV-400-99 |  | FN3280H-400-99-69
6SL3224-0XE42-0UA0 | SINAMICS PM240-IP20-FSGX-U-400V 200.0KW | FN3440-250-119-E2FASXX | FN3450-315-119-E2FASXX | FN3472-315-99-E0XXJXX | FN3482-350-99-E0XXJXX | FN3471-315-99-E0XXJXX | FN3481-315-99-E0XXJXX | FN3473-315-99-E0XXJXX | FN3483-350-99-E0XXJXX | RWK3044-510-99-E0XXX | RWK305-600-S | RWK5420-630-99-E0XXT | FN5060-600-99 | FN5420-630-99-E0XXT | FN3470-315-99-E0XXJXX | FN3480-315-99-E0XXJXX | FN3472-315-99-E0XXJXX | FN3482-350-99-E0XXJXX | FN3471-315-99-E0XXJXX | FN3481-315-99-E0XXJXX | FN3473-315-99-E0XXJXX | FN3483-350-99-E0XXJXX | RWK3044-570-99-E0XXX | RWK305-600-S | RWK5420-630-99-E0XXT | FN5060-600-99 | FN5420-630-99-E0XXT | FN3359-600-99 | FN3270H-600-99 |  | FN3359HV-600-99 |  | FN3280H-600-99-69

## G120 500VAC-690VAC
|  | Drive in Low overload (LO) |  |  | Drive in High overload (HO)
G120 500VAC-690VAC | Power Modul Description | AC Line Reactor LO | dv/dt Filter LO | SineWave Filter LO | AC Line Reactor HO | dv/dt Filter HO | SineWave Filter HO | EMC Filter Motor Cable Lenght ≤ 50m Class C1 | EMC Filter Motor Cable Lenght ≤ 50m Class C2 | EMC Filter for IT Power Networks Class C2
6SL3210-1PH21-4UL0 | SINAMICS PM240-2 IP20-FSD-U-690V-11kW | RWK3062-26-92-E0XXX | FN5060HV-30-99 | FN5040HV-28-84 | RWK3062-21-89-E0XXX | FN5060HV-30-99 | FN5040HV-28-84 | FN3288HV-16-44-C34-R65 | FN3288HV-16-44-C34-R65 | FN3288HVIT-16-44-C43-R65
6SL3210-1PH21-4AL0 | SINAMICS PM240-2 IP20-FSD-A-690V-11kW | RWK3062-26-92-E0XXX | FN5060HV-30-99 | FN5040HV-28-84 | RWK3062-21-89-E0XXX | FN5060HV-30-99 | FN5040HV-28-84 | FN3288HV-16-44-C34-R65 | FN3288HV-16-44-C34-R65 | FN3288HVIT-16-44-C43-R65
6SL3210-1PH22-0UL0 | SINAMICS PM240-2 IP20-FSD-U-690V-15kW | RWK3062-30-92-E0XXX | FN5060HV-30-99 | FN5040HV-28-84 | RWK3062-30-92-E0XXX | FN5060HV-30-99 | FN5040HV-28-84 | FN3288HV-20-33-C36-R65 | FN3288HV-20-33-C36-R65 | FN3288HVIT-20-33-C43-R65
6SL3210-1PH22-0AL0 | SINAMICS PM240-2 IP20-FSD-A-690V-15kW | RWK3062-30-92-E0XXX | FN5060HV-30-99 | FN5040HV-28-84 | RWK3062-30-92-E0XXX | FN5060HV-30-99 | FN5040HV-28-84 | FN3288HV-20-33-C36-R65 | FN3288HV-20-33-C36-R65 | FN3288HVIT-20-33-C43-R65
6SL3210-1PH22-3UL0 | SINAMICS PM240-2 IP20-FSD-U-690V-18,5kW | RWK3062-41-92-E0XXX | FN5060HV-30-99 | FN5040HV-28-84 | RWK3062-41-92-E0XXX | FN5060HV-30-99 | FN5040HV-28-84 | FN3288HV-25-33-C36-R65 | FN3288HV-25-33-C36-R65 | FN3288HVIT-25-33-C43-R65
6SL3210-1PH22-3AL0 | SINAMICS PM240-2 IP20-FSD-A-690V-18,5kW | RWK3062-41-92-E0XXX | FN5060HV-30-99 | FN5040HV-28-84 | RWK3062-41-92-E0XXX | FN5060HV-30-99 | FN5040HV-28-84 | FN3288HV-25-33-C36-R65 | FN3288HV-25-33-C36-R65 | FN3288HVIT-25-33-C43-R65
6SL3210-1PH22-7UL0 | SINAMICS PM240-2 IP20-FSD-U-690V-22kW | RWK3062-51-92-E0XXX | FN5060HV-30-99 | FN5040HV-45-86 | RWK3062-51-92-E0XXX | FN5060HV-45-99 | FN5040HV-45-86 | FN3288HV-25-33-C36-R65 | FN3288HV-25-33-C36-R65 | FN3288HVIT-25-33-C43-R65
6SL3210-1PH22-7AL0 | SINAMICS PM240-2 IP20-FSD-A-690V-22kW | RWK3062-51-92-E0XXX | FN5060HV-30-99 | FN5040HV-45-86 | RWK3062-51-92-E0XXX | FN5060HV-45-99 | FN5040HV-45-86 | FN3288HV-25-33-C36-R65 | FN3288HV-25-33-C36-R65 | FN3288HVIT-25-33-C43-R65
6SL3210-1PH23-5UL0 | SINAMICS PM240-2 IP20-FSD-U-690V-30kW | RWK3062-62-99-E0XXX | FN5060HV-45-99 | FN5040HV-45-86 | RWK3062-62-99-E0XXX | FN5060HV-45-99 | FN5040HV-45-86 | FN3288HV-40-33-C36-R65 | FN3288HV-40-33-C36-R65 | FN3288HVIT-40-33-C43-R65
6SL3210-1PH23-5AL0 | SINAMICS PM240-2 IP20-FSD-A-690V-30kW | RWK3062-62-99-E0XXX | FN5060HV-45-99 | FN5040HV-45-86 | RWK3062-62-99-E0XXX | FN5060HV-45-99 | FN5040HV-45-86 | FN3288HV-40-33-C36-R65 | FN3288HV-40-33-C36-R65 | FN3288HVIT-40-33-C43-R65
6SL3210-1PH24-2UL0 | SINAMICS PM240-2 IP20-FSD-U-690V-37kW | RWK3062-76-99-E0XXX | FN5060HV-75-99 | FN5040HV-75-99 | RWK3062-100-99-E0XXX | FN5060HV-75-99 | FN5040HV-75-99 | FN3288HV-40-33-C36-R65 | FN3288HV-40-33-C36-R65 | FN3288HVIT-40-33-C43-R65
6SL3210-1PH24-2AL0 | SINAMICS PM240-2 IP20-FSD-A-690V-37kW | RWK3062-76-99-E0XXX | FN5060HV-75-99 | FN5040HV-75-99 | RWK3062-100-99-E0XXX | FN5060HV-75-99 | FN5040HV-75-99 | FN3288HV-40-33-C36-R65 | FN3288HV-40-33-C36-R65 | FN3288HVIT-40-33-C43-R65
6SL3210-1PH25-2UL0 | SINAMICS PM240-2 IP20-FSE-U-690V-45kW | RWK3062-100-99-E0XXX | FN5060HV-75-99 | FN5040HV-75-99 | RWK3062-100-99-E0XXX | FN5060HV-75-99 | FN5040HV-75-99 | FN3288HV-50-53-C36-R65 | FN3288HV-50-53-C36-R65 | FN3288HVIT-50-53-C43-R65
6SL3210-1PH25-2AL0 | SINAMICS PM240-2 IP20-FSE-A-690V-45kW | RWK3062-100-99-E0XXX | FN5060HV-75-99 | FN5040HV-75-99 | RWK3062-100-99-E0XXX | FN5060HV-75-99 | FN5040HV-75-99 | FN3288HV-50-53-C36-R65 | FN3288HV-50-53-C36-R65 | FN3288HVIT-50-53-C43-R65
6SL3210-1PH26-2UL0 | SINAMICS PM240-2 IP20-FSE-U-690V-55kW | RWK3062-120-99-E0XXX | FN5060HV-75-99 | FN5040HV-75-99 | RWK3062-120-99-E0XXX | FN5060HV-115-99 | FN5040HV-115-99 | FN3288HV-63-53-C36-R65 | FN3288HV-63-53-C36-R65 | FN3288HVIT-63-53-C43-R65
6SL3210-1PH26-2AL0 | SINAMICS PM240-2 IP20-FSE-A-690V-55kW | RWK3062-120-99-E0XXX | FN5060HV-75-99 | FN5040HV-75-99 | RWK3062-120-99-E0XXX | FN5060HV-115-99 | FN5040HV-115-99 | FN3288HV-63-53-C36-R65 | FN3288HV-63-53-C36-R65 | FN3288HVIT-63-53-C43-R65
6SL3210-1PH28-0UL0 | SINAMICS PM240-2 IP20-FSF-U-690V-75kW | RWK3062-150-99-E0XXX | FN5060HV-115-99 | FN5040HV-115-99 | RWK3062-150-99-E0XXX | FN5060HV-115-99 | FN5040HV-115-99 | FN3288HV-80-34-C36-R65 | FN3288HV-80-34-C36-R65 | FN3288HVIT-80-34-C43-R65
6SL3210-1PH28-0AL0 | SINAMICS PM240-2 IP20-FSF-A-690V-75kW | RWK3062-150-99-E0XXX | FN5060HV-115-99 | FN5040HV-115-99 | RWK3062-150-99-E0XXX | FN5060HV-115-99 | FN5040HV-115-99 | FN3288HV-80-34-C36-R65 | FN3288HV-80-34-C36-R65 | FN3288HVIT-80-34-C43-R65
6SL3210-1PH31-0UL0 | SINAMICS PM240-2 IP20-FSF-U-690V-90kW | RWK3062-180-99-E0XXX | FN5060HV-115-99 | FN5040HV-115-99 | RWK3062-220-99-E0XXX | FN5060HV-165-99 | FN5040HV-165-99 | FN3288HV-100-35-C36-R65 | FN3288HV-100-35-C36-R65 | FN3288HVIT-100-35-C43-R65
6SL3210-1PH31-0AL0 | SINAMICS PM240-2 IP20-FSF-A-690V-90kW | RWK3062-180-99-E0XXX | FN5060HV-115-99 | FN5040HV-115-99 | RWK3062-220-99-E0XXX | FN5060HV-165-99 | FN5040HV-165-99 | FN3288HV-100-35-C36-R65 | FN3288HV-100-35-C36-R65 | FN3288HVIT-100-35-C43-R65
6SL3210-1PH31-2UL0 | SINAMICS PM240-2 IP20-FSF-U-690V-110kW | RWK3062-220-99-E0XXX | FN5060HV-165-99 | FN5040HV-165-99 | RWK3062-280-99-E0XXX | FN5060HV-165-99 | FN5040HV-165-99 | FN3288HV-125-35-C36-R65 | FN3288HV-125-35-C36-R65 | FN3288HVIT-125-35-C44-R65
6SL3210-1PH31-2AL0 | SINAMICS PM240-2 IP20-FSF-A-690V-110kW | RWK3062-220-99-E0XXX | FN5060HV-165-99 | FN5040HV-165-99 | RWK3062-280-99-E0XXX | FN5060HV-165-99 | FN5040HV-165-99 | FN3288HV-125-35-C36-R65 | FN3288HV-125-35-C36-R65 | FN3288HVIT-125-35-C44-R65
6SL3210-1PH31-4UL0 | SINAMICS PM240-2 IP20-FSF-U-690V-132kW | RWK3062-280-99-E0XXX | FN5060HV-165-99 | FN5040HV-165-99 | RWK3062-350-99-E0XXX | FN5060HV-220-99 | FN5040HV-260-99 | FN3288HV-160-40-C36-R65 | FN3288HV-160-40-C36-R65 | FN3288HVIT-160-40-C43-R65
6SL3210-1PH31-4AL0 | SINAMICS PM240-2 IP20-FSF-A-690V-132kW | RWK3062-280-99-E0XXX | FN5060HV-165-99 | FN5040HV-165-99 | RWK3062-350-99-E0XXX | FN5060HV-220-99 | FN5040HV-260-99 | FN3288HV-160-40-C36-R65 | FN3288HV-160-40-C36-R65 | FN3288HVIT-160-40-C43-R65

## G120C 380VAC-480VAC
|  | Drive in Low overload (LO) | [12 empty] | Drive in High overload (HO)
G120C 380VAC-480VAC | Power Modul Description | PHF 5% THDi 400V 50Hz LO | PHF 5% THDi 480V 50Hz LO | PHF 5% THDi 380V 60Hz LO | PHF 5% THDi 480V 60Hz LO | PHF 10-15% THDi 400V 50Hz LO | PHF 10-15% THDi 480V 50Hz LO | PHF 10-15% THDi 400V 60Hz LO | PHF 10-15% THDi 480V 60Hz LO | AC Line Reactor LO | dv/dt Reactor 0.8% LO | dv/dt Reactor 6% LO | dv/dt Filter LO | SineWave Filter LO | PHF 5% THDi 400V 50Hz HO | PHF 5% THDi 480V 50Hz HO | PHF 5% THDi 400V 60Hz HO | PHF 5% THDi 480V 60Hz HO | PHF 10-15% THDi 400V 50Hz HO | PHF 10-15% THDi 480V 50Hz HO | PHF 10-15% THDi 400V 60Hz HO | PHF 10-15% THDi 480V 60Hz HO | AC Line Reactor HO | dv/dt Reactor 0.8% HO | dv/dt Reactor 6% HO | dv/dt Filter HO | SineWave Filter HO | EMC Filter Motor Cable Lenght ≤ 50m Class C1 | EMC Filter Motor Cable Lenght ≤ 50m Class C2 | EMC Filter Low Leakage Current Motor Cable Lenght ≤ 35m Class C2 | EMC Filter for IT Power Networks Class C2 | EMC Filter Motor Cable Lenght > 50m Class C1 | EMC Filter 3-Phase with Neutral for Machine Tools and Low Leakage Current Applications
6SL3210-1KE11-8UB2 | SINAMICS G120C USS/MB 0.55KW | FN3440-1-110-E2XXJRX | FN3450-1-110-E2XXJRX | FN3442-1-110-E2XXJRX | FN3452-1-110-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-5-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-2-88-E0XXX | RWK305-4-KL | RWK5420-2.3-88-E0XXT | FN5060-12-84 | FN5420-2.3-44-E2XXT | FN3440-1-110-E2XXJRX | FN3450-1-110-E2XXJRX | FN3442-1-110-E2XXJRX | FN3452-1-110-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-5-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-2-88-E0XXX | RWK305-4-KL | RWK5420-2.3-88-E0XXT | FN5060-12-84 | FN5420-2.3-44-E2XXT | FN3288-10-44-C34-R65 | FN3287-10-44-C28-R65 | FN3288-10-44-C21-R65 | FN3288IT-10-44-C34-R65 | FN3120H-25-33 | FN3280H-8-29-69
6SL3210-1KE11-8UP2 | SINAMICS G120C DP 0.55KW | FN3440-1-110-E2XXJRX | FN3450-1-110-E2XXJRX | FN3442-1-110-E2XXJRX | FN3452-1-110-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-5-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-2-88-E0XXX | RWK305-4-KL | RWK5420-2.3-88-E0XXT | FN5060-12-84 | FN5420-2.3-44-E2XXT | FN3440-1-110-E2XXJRX | FN3450-1-110-E2XXJRX | FN3442-1-110-E2XXJRX | FN3452-1-110-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-5-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-2-88-E0XXX | RWK305-4-KL | RWK5420-2.3-88-E0XXT | FN5060-12-84 | FN5420-2.3-44-E2XXT | FN3288-10-44-C34-R65 | FN3287-10-44-C28-R65 | FN3288-10-44-C21-R65 | FN3288IT-10-44-C34-R65 | FN3120H-25-33 | FN3280H-8-29-69
6SL3210-1KE11-8UF2 | SINAMICS G120C PN 0.55KW | FN3440-1-110-E2XXJRX | FN3450-1-110-E2XXJRX | FN3442-1-110-E2XXJRX | FN3452-1-110-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-5-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-2-88-E0XXX | RWK305-4-KL | RWK5420-2.3-88-E0XXT | FN5060-12-84 | FN5420-2.3-44-E2XXT | FN3440-1-110-E2XXJRX | FN3450-1-110-E2XXJRX | FN3442-1-110-E2XXJRX | FN3452-1-110-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-5-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-2-88-E0XXX | RWK305-4-KL | RWK5420-2.3-88-E0XXT | FN5060-12-84 | FN5420-2.3-44-E2XXT | FN3288-10-44-C34-R65 | FN3287-10-44-C28-R65 | FN3288-10-44-C21-R65 | FN3288IT-10-44-C34-R65 | FN3120H-25-33 | FN3280H-8-29-69
6SL3210-1KE11-8AB2 | SINAMICS G120C USS/MB 0.55KW | FN3440-1-110-E2XXJRX | FN3450-1-110-E2XXJRX | FN3442-1-110-E2XXJRX | FN3452-1-110-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-5-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-2-88-E0XXX | RWK305-4-KL | RWK5420-2.3-88-E0XXT | FN5060-12-84 | FN5420-2.3-44-E2XXT | FN3440-1-110-E2XXJRX | FN3450-1-110-E2XXJRX | FN3442-1-110-E2XXJRX | FN3452-1-110-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-5-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-2-88-E0XXX | RWK305-4-KL | RWK5420-2.3-88-E0XXT | FN5060-12-84 | FN5420-2.3-44-E2XXT | FN3288-10-44-C34-R65 | FN3287-10-44-C28-R65 | FN3288-10-44-C21-R65 | FN3288IT-10-44-C34-R65 | FN3120H-25-33 | FN3280H-8-29-69
6SL3210-1KE11-8AP2 | SINAMICS G120C DP 0.55KW | FN3440-1-110-E2XXJRX | FN3450-1-110-E2XXJRX | FN3442-1-110-E2XXJRX | FN3452-1-110-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-5-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-2-88-E0XXX | RWK305-4-KL | RWK5420-2.3-88-E0XXT | FN5060-12-84 | FN5420-2.3-44-E2XXT | FN3440-1-110-E2XXJRX | FN3450-1-110-E2XXJRX | FN3442-1-110-E2XXJRX | FN3452-1-110-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-5-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-2-88-E0XXX | RWK305-4-KL | RWK5420-2.3-88-E0XXT | FN5060-12-84 | FN5420-2.3-44-E2XXT | FN3288-10-44-C34-R65 | FN3287-10-44-C28-R65 | FN3288-10-44-C21-R65 | FN3288IT-10-44-C34-R65 | FN3120H-25-33 | FN3280H-8-29-69
6SL3210-1KE11-8AF2 | SINAMICS G120C PN 0.55KW | FN3440-1-110-E2XXJRX | FN3450-1-110-E2XXJRX | FN3442-1-110-E2XXJRX | FN3452-1-110-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-5-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-2-88-E0XXX | RWK305-4-KL | RWK5420-2.3-88-E0XXT | FN5060-12-84 | FN5420-2.3-44-E2XXT | FN3440-1-110-E2XXJRX | FN3450-1-110-E2XXJRX | FN3442-1-110-E2XXJRX | FN3452-1-110-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-5-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-2-88-E0XXX | RWK305-4-KL | RWK5420-2.3-88-E0XXT | FN5060-12-84 | FN5420-2.3-44-E2XXT | FN3288-10-44-C34-R65 | FN3287-10-44-C28-R65 | FN3288-10-44-C21-R65 | FN3288IT-10-44-C34-R65 | FN3120H-25-33 | FN3280H-8-29-69
6SL3210-1KE12-3UB2 | SINAMICS G120C USS/MB 0.75KW | FN3440-1-110-E2XXJRX | FN3450-1-110-E2XXJRX | FN3442-1-110-E2XXJRX | FN3452-1-110-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-5-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-2-88-E0XXX | RWK305-4-KL | RWK5420-3.1-88-E0XXT | FN5060-12-84 | FN5420-3.1-44-E2XXT | FN3440-1-110-E2XXJRX | FN3450-1-110-E2XXJRX | FN3442-1-110-E2XXJRX | FN3452-1-110-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-5-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-2-88-E0XXX | RWK305-4-KL | RWK5420-3.1-88-E0XXT | FN5060-12-84 | FN5420-3.1-44-E2XXT | FN3288-10-44-C34-R65 | FN3287-10-44-C28-R65 | FN3288-10-44-C21-R65 | FN3288IT-10-44-C34-R65 | FN3120H-25-33 | FN3280H-8-29-69
6SL3210-1KE12-3UP2 | SINAMICS G120C DP 0.75KW | FN3440-1-110-E2XXJRX | FN3450-1-110-E2XXJRX | FN3442-1-110-E2XXJRX | FN3452-1-110-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-5-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-2-88-E0XXX | RWK305-4-KL | RWK5420-3.1-88-E0XXT | FN5060-12-84 | FN5420-3.1-44-E2XXT | FN3440-1-110-E2XXJRX | FN3450-1-110-E2XXJRX | FN3442-1-110-E2XXJRX | FN3452-1-110-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-5-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-2-88-E0XXX | RWK305-4-KL | RWK5420-3.1-88-E0XXT | FN5060-12-84 | FN5420-3.1-44-E2XXT | FN3288-10-44-C34-R65 | FN3287-10-44-C28-R65 | FN3288-10-44-C21-R65 | FN3288IT-10-44-C34-R65 | FN3120H-25-33 | FN3280H-8-29-69
6SL3210-1KE12-3UF2 | SINAMICS G120C PN 0.75KW | FN3440-1-110-E2XXJRX | FN3450-1-110-E2XXJRX | FN3442-1-110-E2XXJRX | FN3452-1-110-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-5-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-2-88-E0XXX | RWK305-4-KL | RWK5420-3.1-88-E0XXT | FN5060-12-84 | FN5420-3.1-44-E2XXT | FN3440-1-110-E2XXJRX | FN3450-1-110-E2XXJRX | FN3442-1-110-E2XXJRX | FN3452-1-110-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-5-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-2-88-E0XXX | RWK305-4-KL | RWK5420-3.1-88-E0XXT | FN5060-12-84 | FN5420-3.1-44-E2XXT | FN3288-10-44-C34-R65 | FN3287-10-44-C28-R65 | FN3288-10-44-C21-R65 | FN3288IT-10-44-C34-R65 | FN3120H-25-33 | FN3280H-8-29-69
6SL3210-1KE12-3AB2 | SINAMICS G120C PN 0.75KW | FN3440-1-110-E2XXJRX | FN3450-1-110-E2XXJRX | FN3442-1-110-E2XXJRX | FN3452-1-110-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-5-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-2-88-E0XXX | RWK305-4-KL | RWK5420-3.1-88-E0XXT | FN5060-12-84 | FN5420-3.1-44-E2XXT | FN3440-1-110-E2XXJRX | FN3450-1-110-E2XXJRX | FN3442-1-110-E2XXJRX | FN3452-1-110-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-5-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-2-88-E0XXX | RWK305-4-KL | RWK5420-3.1-88-E0XXT | FN5060-12-84 | FN5420-3.1-44-E2XXT | FN3288-10-44-C34-R65 | FN3287-10-44-C28-R65 | FN3288-10-44-C21-R65 | FN3288IT-10-44-C34-R65 | FN3120H-25-33 | FN3280H-8-29-69
6SL3210-1KE12-3AP2 | SINAMICS G120C DP 0.75KW | FN3440-1-110-E2XXJRX | FN3450-1-110-E2XXJRX | FN3442-1-110-E2XXJRX | FN3452-1-110-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-5-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-2-88-E0XXX | RWK305-4-KL | RWK5420-3.1-88-E0XXT | FN5060-12-84 | FN5420-3.1-44-E2XXT | FN3440-1-110-E2XXJRX | FN3450-1-110-E2XXJRX | FN3442-1-110-E2XXJRX | FN3452-1-110-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-5-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-2-88-E0XXX | RWK305-4-KL | RWK5420-3.1-88-E0XXT | FN5060-12-84 | FN5420-3.1-44-E2XXT | FN3288-10-44-C34-R65 | FN3287-10-44-C28-R65 | FN3288-10-44-C21-R65 | FN3288IT-10-44-C34-R65 | FN3120H-25-33 | FN3280H-8-29-69
6SL3210-1KE12-3AF2 | SINAMICS G120C PN 0.75KW | FN3440-1-110-E2XXJRX | FN3450-1-110-E2XXJRX | FN3442-1-110-E2XXJRX | FN3452-1-110-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-5-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-2-88-E0XXX | RWK305-4-KL | RWK5420-3.1-88-E0XXT | FN5060-12-84 | FN5420-3.1-44-E2XXT | FN3440-1-110-E2XXJRX | FN3450-1-110-E2XXJRX | FN3442-1-110-E2XXJRX | FN3452-1-110-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-5-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-2-88-E0XXX | RWK305-4-KL | RWK5420-3.1-88-E0XXT | FN5060-12-84 | FN5420-3.1-44-E2XXT | FN3288-10-44-C34-R65 | FN3287-10-44-C28-R65 | FN3288-10-44-C21-R65 | FN3288IT-10-44-C34-R65 | FN3120H-25-33 | FN3280H-8-29-69
6SL3210-1KE13-2UB2 | SINAMICS G120C USS/MB 1.1KW | FN3440-1-110-E2XXJRX | FN3450-2-110-E2XXJRX | FN3442-2-110-E2XXJRX | FN3452-1-110-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-5-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-3.5-88-E0XXX | RWK305-4-KL | RWK5420-5.9-88-E0XXT | FN5060-12-84 | FN5420-5.9-44-E2FXT | FN3440-1-110-E2XXJRX | FN3450-2-110-E2XXJRX | FN3442-1-110-E2XXJRX | FN3452-1-110-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-5-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-3.5-88-E0XXX | RWK305-4-KL | RWK5420-5.9-88-E0XXT | FN5060-12-84 | FN5420-5.9-44-E2FXT | FN3288-10-44-C34-R65 | FN3287-10-44-C28-R65 | FN3288-10-44-C21-R65 | FN3288IT-10-44-C34-R65 | FN3120H-25-33 | FN3280H-8-29-69
6SL3210-1KE13-2UP2 | SINAMICS G120C DP 1.1KW | FN3440-1-110-E2XXJRX | FN3450-2-110-E2XXJRX | FN3442-2-110-E2XXJRX | FN3452-1-110-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-5-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-3.5-88-E0XXX | RWK305-4-KL | RWK5420-5.9-88-E0XXT | FN5060-12-84 | FN5420-5.9-44-E2FXT | FN3440-1-110-E2XXJRX | FN3450-2-110-E2XXJRX | FN3442-1-110-E2XXJRX | FN3452-1-110-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-5-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-3.5-88-E0XXX | RWK305-4-KL | RWK5420-5.9-88-E0XXT | FN5060-12-84 | FN5420-5.9-44-E2FXT | FN3288-10-44-C34-R65 | FN3287-10-44-C28-R65 | FN3288-10-44-C21-R65 | FN3288IT-10-44-C34-R65 | FN3120H-25-33 | FN3280H-8-29-69
6SL3210-1KE13-2UF2 | SINAMICS G120C PN 1.1KW | FN3440-1-110-E2XXJRX | FN3450-2-110-E2XXJRX | FN3442-2-110-E2XXJRX | FN3452-1-110-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-5-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-3.5-88-E0XXX | RWK305-4-KL | RWK5420-5.9-88-E0XXT | FN5060-12-84 | FN5420-5.9-44-E2FXT | FN3440-1-110-E2XXJRX | FN3450-2-110-E2XXJRX | FN3442-1-110-E2XXJRX | FN3452-1-110-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-5-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-3.5-88-E0XXX | RWK305-4-KL | RWK5420-5.9-88-E0XXT | FN5060-12-84 | FN5420-5.9-44-E2FXT | FN3288-10-44-C34-R65 | FN3287-10-44-C28-R65 | FN3288-10-44-C21-R65 | FN3288IT-10-44-C34-R65 | FN3120H-25-33 | FN3280H-8-29-69
6SL3210-1KE13-2AB2 | SINAMICS G120C USS/MB 1.1KW | FN3440-1-110-E2XXJRX | FN3450-2-110-E2XXJRX | FN3442-2-110-E2XXJRX | FN3452-1-110-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-5-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-3.5-88-E0XXX | RWK305-4-KL | RWK5420-5.9-88-E0XXT | FN5060-12-84 | FN5420-5.9-44-E2FXT | FN3440-1-110-E2XXJRX | FN3450-2-110-E2XXJRX | FN3442-1-110-E2XXJRX | FN3452-1-110-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-5-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-3.5-88-E0XXX | RWK305-4-KL | RWK5420-5.9-88-E0XXT | FN5060-12-84 | FN5420-5.9-44-E2FXT | FN3288-10-44-C34-R65 | FN3287-10-44-C28-R65 | FN3288-10-44-C21-R65 | FN3288IT-10-44-C34-R65 | FN3120H-25-33 | FN3280H-8-29-69
6SL3210-1KE13-2AP2 | SINAMICS G120C DP 1.1KW | FN3440-1-110-E2XXJRX | FN3450-2-110-E2XXJRX | FN3442-2-110-E2XXJRX | FN3452-1-110-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-5-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-3.5-88-E0XXX | RWK305-4-KL | RWK5420-5.9-88-E0XXT | FN5060-12-84 | FN5420-5.9-44-E2FXT | FN3440-1-110-E2XXJRX | FN3450-2-110-E2XXJRX | FN3442-1-110-E2XXJRX | FN3452-1-110-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-5-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-3.5-88-E0XXX | RWK305-4-KL | RWK5420-5.9-88-E0XXT | FN5060-12-84 | FN5420-5.9-44-E2FXT | FN3288-10-44-C34-R65 | FN3287-10-44-C28-R65 | FN3288-10-44-C21-R65 | FN3288IT-10-44-C34-R65 | FN3120H-25-33 | FN3280H-8-29-69
6SL3210-1KE13-2AF2 | SINAMICS G120C PN 1.1KW | FN3440-1-110-E2XXJRX | FN3450-2-110-E2XXJRX | FN3442-2-110-E2XXJRX | FN3452-1-110-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-5-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-3.5-88-E0XXX | RWK305-4-KL | RWK5420-5.9-88-E0XXT | FN5060-12-84 | FN5420-5.9-44-E2FXT | FN3440-1-110-E2XXJRX | FN3450-2-110-E2XXJRX | FN3442-1-110-E2XXJRX | FN3452-1-110-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-5-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-3.5-88-E0XXX | RWK305-4-KL | RWK5420-5.9-88-E0XXT | FN5060-12-84 | FN5420-5.9-44-E2FXT | FN3288-10-44-C34-R65 | FN3287-10-44-C28-R65 | FN3288-10-44-C21-R65 | FN3288IT-10-44-C34-R65 | FN3120H-25-33 | FN3280H-8-29-69
6SL3210-1KE14-3UB2 | SINAMICS G120C USS/MB 1.5KW | FN3440-1-110-E2XXJRX | FN3450-2-110-E2XXJRX | FN3442-2-110-E2XXJRX | FN3452-3-110-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-5-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-3.5-88-E0XXX | RWK305-7.8-KL | RWK5420-5.9-88-E0XXT | FN5060-12-84 | FN5420-5.9-44-E2FXT | FN3440-1-110-E2XXJRX | FN3450-2-110-E2XXJRX | FN3442-2-110-E2XXJRX | FN3452-3-110-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-5-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-3.5-88-E0XXX | RWK305-7.8-KL | RWK5420-5.9-88-E0XXT | FN5060-12-84 | FN5420-5.9-44-E2FXT | FN3288-10-44-C34-R65 | FN3287-10-44-C28-R65 | FN3288-10-44-C21-R65 | FN3288IT-10-44-C34-R65 | FN3120H-25-33 | FN3280H-8-29-69
6SL3210-1KE14-3UP2 | SINAMICS G120C DP 1.5KW | FN3440-1-110-E2XXJRX | FN3450-2-110-E2XXJRX | FN3442-2-110-E2XXJRX | FN3452-3-110-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-5-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-3.5-88-E0XXX | RWK305-7.8-KL | RWK5420-5.9-88-E0XXT | FN5060-12-84 | FN5420-5.9-44-E2FXT | FN3440-1-110-E2XXJRX | FN3450-2-110-E2XXJRX | FN3442-2-110-E2XXJRX | FN3452-3-110-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-5-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-3.5-88-E0XXX | RWK305-7.8-KL | RWK5420-5.9-88-E0XXT | FN5060-12-84 | FN5420-5.9-44-E2FXT | FN3288-10-44-C34-R65 | FN3287-10-44-C28-R65 | FN3288-10-44-C21-R65 | FN3288IT-10-44-C34-R65 | FN3120H-25-33 | FN3280H-8-29-69
6SL3210-1KE14-3UF2 | SINAMICS G120C PN 1.5KW | FN3440-1-110-E2XXJRX | FN3450-2-110-E2XXJRX | FN3442-2-110-E2XXJRX | FN3452-3-110-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-5-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-3.5-88-E0XXX | RWK305-7.8-KL | RWK5420-5.9-88-E0XXT | FN5060-12-84 | FN5420-5.9-44-E2FXT | FN3440-1-110-E2XXJRX | FN3450-2-110-E2XXJRX | FN3442-2-110-E2XXJRX | FN3452-3-110-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-5-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-3.5-88-E0XXX | RWK305-7.8-KL | RWK5420-5.9-88-E0XXT | FN5060-12-84 | FN5420-5.9-44-E2FXT | FN3288-10-44-C34-R65 | FN3287-10-44-C28-R65 | FN3288-10-44-C21-R65 | FN3288IT-10-44-C34-R65 | FN3120H-25-33 | FN3280H-8-29-69
6SL3210-1KE14-3AB2 | SINAMICS G120C USS/MB 1.5KW | FN3440-1-110-E2XXJRX | FN3450-2-110-E2XXJRX | FN3442-2-110-E2XXJRX | FN3452-3-110-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-5-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-3.5-88-E0XXX | RWK305-7.8-KL | RWK5420-5.9-88-E0XXT | FN5060-12-84 | FN5420-5.9-44-E2FXT | FN3440-1-110-E2XXJRX | FN3450-2-110-E2XXJRX | FN3442-2-110-E2XXJRX | FN3452-3-110-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-5-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-3.5-88-E0XXX | RWK305-7.8-KL | RWK5420-5.9-88-E0XXT | FN5060-12-84 | FN5420-5.9-44-E2FXT | FN3288-10-44-C34-R65 | FN3287-10-44-C28-R65 | FN3288-10-44-C21-R65 | FN3288IT-10-44-C34-R65 | FN3120H-25-33 | FN3280H-8-29-69
6SL3210-1KE14-3AP2 | SINAMICS G120C DP 1.5KW | FN3440-1-110-E2XXJRX | FN3450-2-110-E2XXJRX | FN3442-2-110-E2XXJRX | FN3452-3-110-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-5-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-3.5-88-E0XXX | RWK305-7.8-KL | RWK5420-5.9-88-E0XXT | FN5060-12-84 | FN5420-5.9-44-E2FXT | FN3440-1-110-E2XXJRX | FN3450-2-110-E2XXJRX | FN3442-2-110-E2XXJRX | FN3452-3-110-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-5-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-3.5-88-E0XXX | RWK305-7.8-KL | RWK5420-5.9-88-E0XXT | FN5060-12-84 | FN5420-5.9-44-E2FXT | FN3288-10-44-C34-R65 | FN3287-10-44-C28-R65 | FN3288-10-44-C21-R65 | FN3288IT-10-44-C34-R65 | FN3120H-25-33 | FN3280H-8-29-69
6SL3210-1KE14-3AF2 | SINAMICS G120C PN 1.5KW | FN3440-1-110-E2XXJRX | FN3450-2-110-E2XXJRX | FN3442-2-110-E2XXJRX | FN3452-3-110-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-5-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-3.5-88-E0XXX | RWK305-7.8-KL | RWK5420-5.9-88-E0XXT | FN5060-12-84 | FN5420-5.9-44-E2FXT | FN3440-1-110-E2XXJRX | FN3450-2-110-E2XXJRX | FN3442-2-110-E2XXJRX | FN3452-3-110-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-5-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-3.5-88-E0XXX | RWK305-7.8-KL | RWK5420-5.9-88-E0XXT | FN5060-12-84 | FN5420-5.9-44-E2FXT | FN3288-10-44-C34-R65 | FN3287-10-44-C28-R65 | FN3288-10-44-C21-R65 | FN3288IT-10-44-C34-R65 | FN3120H-25-33 | FN3280H-8-29-69
6SL3210-1KE15-8UB2 | SINAMICS G120C USS/MB 2.2KW | FN3440-2-110-E2XXJRX | FN3450-4-112-E2XXJRX | FN3442-4-112-E2XXJRX | FN3452-3-110-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-5-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-6.5-88-E0XXX | RWK305-7.8-KL | RWK5420-10-88-E0XXT | FN5060-12-84 | FN5420-10-44-E2FXT | FN3440-2-110-E2XXJRX | FN3450-4-112-E2XXJRX | FN3442-2-110-E2XXJRX | FN3452-3-110-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-5-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-6.5-88-E0XXX | RWK305-7.8-KL | RWK5420-10-88-E0XXT | FN5060-12-84 | FN5420-10-44-E2FXT | FN3288-10-44-C34-R65 | FN3287-10-44-C28-R65 | FN3288-10-44-C21-R65 | FN3288IT-10-44-C34-R65 | FN3120H-25-33 | FN3280H-8-29-69
6SL3210-1KE15-8UP2 | SINAMICS G120C DP 2.2KW | FN3440-2-110-E2XXJRX | FN3450-4-112-E2XXJRX | FN3442-4-112-E2XXJRX | FN3452-3-110-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-5-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-6.5-88-E0XXX | RWK305-7.8-KL | RWK5420-10-88-E0XXT | FN5060-12-84 | FN5420-10-44-E2FXT | FN3440-2-110-E2XXJRX | FN3450-4-112-E2XXJRX | FN3442-2-110-E2XXJRX | FN3452-3-110-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-5-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-6.5-88-E0XXX | RWK305-7.8-KL | RWK5420-10-88-E0XXT | FN5060-12-84 | FN5420-10-44-E2FXT | FN3288-10-44-C34-R65 | FN3287-10-44-C28-R65 | FN3288-10-44-C21-R65 | FN3288IT-10-44-C34-R65 | FN3120H-25-33 | FN3280H-8-29-69
6SL3210-1KE15-8UF2 | SINAMICS G120C PN 2.2KW | FN3440-2-110-E2XXJRX | FN3450-4-112-E2XXJRX | FN3442-4-112-E2XXJRX | FN3452-3-110-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-5-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-6.5-88-E0XXX | RWK305-7.8-KL | RWK5420-10-88-E0XXT | FN5060-12-84 | FN5420-10-44-E2FXT | FN3440-2-110-E2XXJRX | FN3450-4-112-E2XXJRX | FN3442-2-110-E2XXJRX | FN3452-3-110-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-5-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-6.5-88-E0XXX | RWK305-7.8-KL | RWK5420-10-88-E0XXT | FN5060-12-84 | FN5420-10-44-E2FXT | FN3288-10-44-C34-R65 | FN3287-10-44-C28-R65 | FN3288-10-44-C21-R65 | FN3288IT-10-44-C34-R65 | FN3120H-25-33 | FN3280H-8-29-69
6SL3210-1KE15-8AB2 | SINAMICS G120C USS/MB 2.2KW | FN3440-2-110-E2XXJRX | FN3450-4-112-E2XXJRX | FN3442-4-112-E2XXJRX | FN3452-3-110-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-5-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-6.5-88-E0XXX | RWK305-7.8-KL | RWK5420-10-88-E0XXT | FN5060-12-84 | FN5420-10-44-E2FXT | FN3440-2-110-E2XXJRX | FN3450-4-112-E2XXJRX | FN3442-2-110-E2XXJRX | FN3452-3-110-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-5-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-6.5-88-E0XXX | RWK305-7.8-KL | RWK5420-10-88-E0XXT | FN5060-12-84 | FN5420-10-44-E2FXT | FN3288-10-44-C34-R65 | FN3287-10-44-C28-R65 | FN3288-10-44-C21-R65 | FN3288IT-10-44-C34-R65 | FN3120H-25-33 | FN3280H-8-29-69
6SL3210-1KE15-8AP2 | SINAMICS G120C DP 2.2KW | FN3440-2-110-E2XXJRX | FN3450-4-112-E2XXJRX | FN3442-4-112-E2XXJRX | FN3452-3-110-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-5-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-6.5-88-E0XXX | RWK305-7.8-KL | RWK5420-10-88-E0XXT | FN5060-12-84 | FN5420-10-44-E2FXT | FN3440-2-110-E2XXJRX | FN3450-4-112-E2XXJRX | FN3442-2-110-E2XXJRX | FN3452-3-110-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-5-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-6.5-88-E0XXX | RWK305-7.8-KL | RWK5420-10-88-E0XXT | FN5060-12-84 | FN5420-10-44-E2FXT | FN3288-10-44-C34-R65 | FN3287-10-44-C28-R65 | FN3288-10-44-C21-R65 | FN3288IT-10-44-C34-R65 | FN3120H-25-33 | FN3280H-8-29-69
6SL3210-1KE15-8AF2 | SINAMICS G120C PN 2.2KW | FN3440-2-110-E2XXJRX | FN3450-4-112-E2XXJRX | FN3442-4-112-E2XXJRX | FN3452-3-110-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-5-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-6.5-88-E0XXX | RWK305-7.8-KL | RWK5420-10-88-E0XXT | FN5060-12-84 | FN5420-10-44-E2FXT | FN3440-2-110-E2XXJRX | FN3450-4-112-E2XXJRX | FN3442-2-110-E2XXJRX | FN3452-3-110-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-5-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-6.5-88-E0XXX | RWK305-7.8-KL | RWK5420-10-88-E0XXT | FN5060-12-84 | FN5420-10-44-E2FXT | FN3288-10-44-C34-R65 | FN3287-10-44-C28-R65 | FN3288-10-44-C21-R65 | FN3288IT-10-44-C34-R65 | FN3120H-25-33 | FN3280H-8-29-69
6SL3210-1KE17-5UB1 | SINAMICS G120C USS/MB 3.0KW | FN3440-4-112-E2XXJRX | FN3450-4-112-E2XXJRX | FN3442-4-112-E2XXJRX | FN3452-5-112-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-5-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-6.5-88-E0XXX | RWK305-10-KL | RWK5420-10-88-E0XXT | FN5060-12-84 | FN5420-10-44-E2FXT | FN3440-4-112-E2XXJRX | FN3450-4-112-E2XXJRX | FN3442-4-112-E2XXJRX | FN3452-5-112-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-5-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-6.5-88-E0XXX | RWK305-10-KL | RWK5420-10-88-E0XXT | FN5060-12-84 | FN5420-10-44-E2FXT | FN3288-10-44-C34-R65 | FN3287-10-44-C28-R65 | FN3288-10-44-C21-R65 | FN3288IT-10-44-C34-R65 | FN3120H-25-33 | FN3280H-16-29-69
6SL3210-1KE17-5UP1 | SINAMICS G120C DP 3.0KW | FN3440-4-112-E2XXJRX | FN3450-4-112-E2XXJRX | FN3442-4-112-E2XXJRX | FN3452-5-112-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-5-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-6.5-88-E0XXX | RWK305-10-KL | RWK5420-10-88-E0XXT | FN5060-12-84 | FN5420-10-44-E2FXT | FN3440-4-112-E2XXJRX | FN3450-4-112-E2XXJRX | FN3442-4-112-E2XXJRX | FN3452-5-112-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-5-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-6.5-88-E0XXX | RWK305-10-KL | RWK5420-10-88-E0XXT | FN5060-12-84 | FN5420-10-44-E2FXT | FN3288-10-44-C34-R65 | FN3287-10-44-C28-R65 | FN3288-10-44-C21-R65 | FN3288IT-10-44-C34-R65 | FN3120H-25-33 | FN3280H-16-29-69
6SL3210-1KE17-5UF1 | SINAMICS G120C PN 3.0KW | FN3440-4-112-E2XXJRX | FN3450-4-112-E2XXJRX | FN3442-4-112-E2XXJRX | FN3452-5-112-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-5-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-6.5-88-E0XXX | RWK305-10-KL | RWK5420-10-88-E0XXT | FN5060-12-84 | FN5420-10-44-E2FXT | FN3440-4-112-E2XXJRX | FN3450-4-112-E2XXJRX | FN3442-4-112-E2XXJRX | FN3452-5-112-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-5-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-6.5-88-E0XXX | RWK305-10-KL | RWK5420-10-88-E0XXT | FN5060-12-84 | FN5420-10-44-E2FXT | FN3288-10-44-C34-R65 | FN3287-10-44-C28-R65 | FN3288-10-44-C21-R65 | FN3288IT-10-44-C34-R65 | FN3120H-25-33 | FN3280H-16-29-69
6SL3210-1KE17-5AB1 | SINAMICS G120C USS/MB 3.0KW | FN3440-4-112-E2XXJRX | FN3450-4-112-E2XXJRX | FN3442-4-112-E2XXJRX | FN3452-5-112-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-5-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-6.5-88-E0XXX | RWK305-10-KL | RWK5420-10-88-E0XXT | FN5060-12-84 | FN5420-10-44-E2FXT | FN3440-4-112-E2XXJRX | FN3450-4-112-E2XXJRX | FN3442-4-112-E2XXJRX | FN3452-5-112-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-5-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-6.5-88-E0XXX | RWK305-10-KL | RWK5420-10-88-E0XXT | FN5060-12-84 | FN5420-10-44-E2FXT | FN3288-10-44-C34-R65 | FN3287-10-44-C28-R65 | FN3288-10-44-C21-R65 | FN3288IT-10-44-C34-R65 | FN3120H-25-33 | FN3280H-16-29-69
6SL3210-1KE17-5AP1 | SINAMICS G120C DP 3.0KW | FN3440-4-112-E2XXJRX | FN3450-4-112-E2XXJRX | FN3442-4-112-E2XXJRX | FN3452-5-112-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-5-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-6.5-88-E0XXX | RWK305-10-KL | RWK5420-10-88-E0XXT | FN5060-12-84 | FN5420-10-44-E2FXT | FN3440-4-112-E2XXJRX | FN3450-4-112-E2XXJRX | FN3442-4-112-E2XXJRX | FN3452-5-112-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-5-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-6.5-88-E0XXX | RWK305-10-KL | RWK5420-10-88-E0XXT | FN5060-12-84 | FN5420-10-44-E2FXT | FN3288-10-44-C34-R65 | FN3287-10-44-C28-R65 | FN3288-10-44-C21-R65 | FN3288IT-10-44-C34-R65 | FN3120H-25-33 | FN3280H-16-29-69
6SL3210-1KE17-5AF1 | SINAMICS G120C PN 3.0KW | FN3440-4-112-E2XXJRX | FN3450-4-112-E2XXJRX | FN3442-4-112-E2XXJRX | FN3452-5-112-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-5-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-6.5-88-E0XXX | RWK305-10-KL | RWK5420-10-88-E0XXT | FN5060-12-84 | FN5420-10-44-E2FXT | FN3440-4-112-E2XXJRX | FN3450-4-112-E2XXJRX | FN3442-4-112-E2XXJRX | FN3452-5-112-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-5-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-6.5-88-E0XXX | RWK305-10-KL | RWK5420-10-88-E0XXT | FN5060-12-84 | FN5420-10-44-E2FXT | FN3288-10-44-C34-R65 | FN3287-10-44-C28-R65 | FN3288-10-44-C21-R65 | FN3288IT-10-44-C34-R65 | FN3120H-25-33 | FN3280H-16-29-69
6SL3210-1KE18-8UB1 | SINAMICS G120C USS/MB 4.0KW | FN3440-4-112-E2XXJRX | FN3450-6-112-E2XXJRX | FN3442-6-112-E2XXJRX | FN3452-5-112-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-8-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-9-88-E0XXX | RWK305-10-KL | RWK5420-10-88-E0XXT | FN5060-12-84 | FN5420-10-44-E2FXT | FN3440-4-112-E2XXJRX | FN3450-6-112-E2XXJRX | FN3442-6-112-E2XXJRX | FN3452-5-112-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-8-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-9-88-E0XXX | RWK305-14-KL | RWK5420-13-89-E0XXT | FN5060-12-84 | FN5420-13-33-E2FXT | FN3288-16-44-C35-R65 | FN3287-16-44-C33-R65 | FN3288-16-44-C21-R65 | FN3288IT-16-44-C34-R65 | FN3120H-25-33 | FN3280H-16-29-69
6SL3210-1KE18-8UP1 | SINAMICS G120C DP 4.0KW | FN3440-4-112-E2XXJRX | FN3450-6-112-E2XXJRX | FN3442-6-112-E2XXJRX | FN3452-5-112-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-8-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-9-88-E0XXX | RWK305-10-KL | RWK5420-10-88-E0XXT | FN5060-12-84 | FN5420-10-44-E2FXT | FN3440-4-112-E2XXJRX | FN3450-6-112-E2XXJRX | FN3442-6-112-E2XXJRX | FN3452-5-112-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-8-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-9-88-E0XXX | RWK305-14-KL | RWK5420-13-89-E0XXT | FN5060-12-84 | FN5420-13-33-E2FXT | FN3288-16-44-C35-R65 | FN3287-16-44-C33-R65 | FN3288-16-44-C21-R65 | FN3288IT-16-44-C34-R65 | FN3120H-25-33 | FN3280H-16-29-69
6SL3210-1KE18-8UF1 | SINAMICS G120C PN 4.0KW | FN3440-4-112-E2XXJRX | FN3450-6-112-E2XXJRX | FN3442-6-112-E2XXJRX | FN3452-5-112-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-8-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-9-88-E0XXX | RWK305-10-KL | RWK5420-10-88-E0XXT | FN5060-12-84 | FN5420-10-44-E2FXT | FN3440-4-112-E2XXJRX | FN3450-6-112-E2XXJRX | FN3442-6-112-E2XXJRX | FN3452-5-112-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-8-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-9-88-E0XXX | RWK305-14-KL | RWK5420-13-89-E0XXT | FN5060-12-84 | FN5420-13-33-E2FXT | FN3288-16-44-C35-R65 | FN3287-16-44-C33-R65 | FN3288-16-44-C21-R65 | FN3288IT-16-44-C34-R65 | FN3120H-25-33 | FN3280H-16-29-69
6SL3210-1KE18-8AB1 | SINAMICS G120C USS/MB 4.0KW | FN3440-4-112-E2XXJRX | FN3450-6-112-E2XXJRX | FN3442-6-112-E2XXJRX | FN3452-5-112-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-8-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-9-88-E0XXX | RWK305-10-KL | RWK5420-10-88-E0XXT | FN5060-12-84 | FN5420-10-44-E2FXT | FN3440-4-112-E2XXJRX | FN3450-6-112-E2XXJRX | FN3442-6-112-E2XXJRX | FN3452-5-112-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-8-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-9-88-E0XXX | RWK305-14-KL | RWK5420-13-89-E0XXT | FN5060-12-84 | FN5420-13-33-E2FXT | FN3288-16-44-C35-R65 | FN3287-16-44-C33-R65 | FN3288-16-44-C21-R65 | FN3288IT-16-44-C34-R65 | FN3120H-25-33 | FN3280H-16-29-69
6SL3210-1KE18-8AP1 | SINAMICS G120C DP 4.0KW | FN3440-4-112-E2XXJRX | FN3450-6-112-E2XXJRX | FN3442-6-112-E2XXJRX | FN3452-5-112-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-8-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-9-88-E0XXX | RWK305-10-KL | RWK5420-10-88-E0XXT | FN5060-12-84 | FN5420-10-44-E2FXT | FN3440-4-112-E2XXJRX | FN3450-6-112-E2XXJRX | FN3442-6-112-E2XXJRX | FN3452-5-112-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-8-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-9-88-E0XXX | RWK305-14-KL | RWK5420-13-89-E0XXT | FN5060-12-84 | FN5420-13-33-E2FXT | FN3288-16-44-C35-R65 | FN3287-16-44-C33-R65 | FN3288-16-44-C21-R65 | FN3288IT-16-44-C34-R65 | FN3120H-25-33 | FN3280H-16-29-69
6SL3210-1KE18-8AF1 | SINAMICS G120C PN 4.0KW | FN3440-4-112-E2XXJRX | FN3450-6-112-E2XXJRX | FN3442-6-112-E2XXJRX | FN3452-5-112-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-8-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-9-88-E0XXX | RWK305-10-KL | RWK5420-10-88-E0XXT | FN5060-12-84 | FN5420-10-44-E2FXT | FN3440-4-112-E2XXJRX | FN3450-6-112-E2XXJRX | FN3442-6-112-E2XXJRX | FN3452-5-112-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-8-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-9-88-E0XXX | RWK305-14-KL | RWK5420-13-89-E0XXT | FN5060-12-84 | FN5420-13-33-E2FXT | FN3288-16-44-C35-R65 | FN3287-16-44-C33-R65 | FN3288-16-44-C21-R65 | FN3288IT-16-44-C34-R65 | FN3120H-25-33 | FN3280H-16-29-69
6SL3210-1KE21-3UB1 | SINAMICS G120C USS/MB 5.5KW | FN3440-6-112-E2XXJRX | FN3450-6-112-E2XXJRX | FN3442-6-112-E2XXJRX | FN3452-8-112-E2XXJRX | FN3446-6-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-10-44-E2XXJXX | FN3458-8-44-E2XXJXX | RWK3044-12-88-E0XXX | RWK305-14-KL | RWK5420-18-89-E0XXT | FN5060-24-84 | FN5420-18-33-E2FXT | FN3440-6-112-E2XXJRX | FN3450-6-112-E2XXJRX | FN3442-6-112-E2XXJRX | FN3452-8-112-E2XXJRX | FN3446-6-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-10-44-E2XXJXX | FN3458-8-44-E2XXJXX | RWK3044-12-88-E0XXX | RWK305-14-KL | RWK5420-13-89-E0XXT | FN5060-24-84 | FN5420-13-33-E2FXT | FN3288-20-33-C35-R65 | FN3287-20-33-C33-R65 | FN3288-20-33-C21-R65 | FN3288IT-20-33-C34-R65 | FN3120H-25-33 | FN3280H-25-33-69
6SL3210-1KE21-3UP1 | SINAMICS G120C DP 5.5KW | FN3440-6-112-E2XXJRX | FN3450-6-112-E2XXJRX | FN3442-6-112-E2XXJRX | FN3452-8-112-E2XXJRX | FN3446-6-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-10-44-E2XXJXX | FN3458-8-44-E2XXJXX | RWK3044-12-88-E0XXX | RWK305-14-KL | RWK5420-18-89-E0XXT | FN5060-24-84 | FN5420-18-33-E2FXT | FN3440-6-112-E2XXJRX | FN3450-6-112-E2XXJRX | FN3442-6-112-E2XXJRX | FN3452-8-112-E2XXJRX | FN3446-6-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-10-44-E2XXJXX | FN3458-8-44-E2XXJXX | RWK3044-12-88-E0XXX | RWK305-14-KL | RWK5420-13-89-E0XXT | FN5060-24-84 | FN5420-13-33-E2FXT | FN3288-20-33-C35-R65 | FN3287-20-33-C33-R65 | FN3288-20-33-C21-R65 | FN3288IT-20-33-C34-R65 | FN3120H-25-33 | FN3280H-25-33-69
6SL3210-1KE21-3UF1 | SINAMICS G120C PN 5.5KW | FN3440-6-112-E2XXJRX | FN3450-6-112-E2XXJRX | FN3442-6-112-E2XXJRX | FN3452-8-112-E2XXJRX | FN3446-6-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-10-44-E2XXJXX | FN3458-8-44-E2XXJXX | RWK3044-12-88-E0XXX | RWK305-14-KL | RWK5420-18-89-E0XXT | FN5060-24-84 | FN5420-18-33-E2FXT | FN3440-6-112-E2XXJRX | FN3450-6-112-E2XXJRX | FN3442-6-112-E2XXJRX | FN3452-8-112-E2XXJRX | FN3446-6-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-10-44-E2XXJXX | FN3458-8-44-E2XXJXX | RWK3044-12-88-E0XXX | RWK305-14-KL | RWK5420-13-89-E0XXT | FN5060-24-84 | FN5420-13-33-E2FXT | FN3288-20-33-C35-R65 | FN3287-20-33-C33-R65 | FN3288-20-33-C21-R65 | FN3288IT-20-33-C34-R65 | FN3120H-25-33 | FN3280H-25-33-69
6SL3210-1KE21-3AB1 | SINAMICS G120C USS/MB 5.5KW | FN3440-6-112-E2XXJRX | FN3450-6-112-E2XXJRX | FN3442-6-112-E2XXJRX | FN3452-8-112-E2XXJRX | FN3446-6-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-10-44-E2XXJXX | FN3458-8-44-E2XXJXX | RWK3044-12-88-E0XXX | RWK305-14-KL | RWK5420-18-89-E0XXT | FN5060-24-84 | FN5420-18-33-E2FXT | FN3440-6-112-E2XXJRX | FN3450-6-112-E2XXJRX | FN3442-6-112-E2XXJRX | FN3452-8-112-E2XXJRX | FN3446-6-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-10-44-E2XXJXX | FN3458-8-44-E2XXJXX | RWK3044-12-88-E0XXX | RWK305-14-KL | RWK5420-13-89-E0XXT | FN5060-24-84 | FN5420-13-33-E2FXT | FN3288-20-33-C35-R65 | FN3287-20-33-C33-R65 | FN3288-20-33-C21-R65 | FN3288IT-20-33-C34-R65 | FN3120H-25-33 | FN3280H-25-33-69
6SL3210-1KE21-3AP1 | SINAMICS G120C DP 5.5KW | FN3440-6-112-E2XXJRX | FN3450-6-112-E2XXJRX | FN3442-6-112-E2XXJRX | FN3452-8-112-E2XXJRX | FN3446-6-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-10-44-E2XXJXX | FN3458-8-44-E2XXJXX | RWK3044-12-88-E0XXX | RWK305-14-KL | RWK5420-18-89-E0XXT | FN5060-24-84 | FN5420-18-33-E2FXT | FN3440-6-112-E2XXJRX | FN3450-6-112-E2XXJRX | FN3442-6-112-E2XXJRX | FN3452-8-112-E2XXJRX | FN3446-6-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-10-44-E2XXJXX | FN3458-8-44-E2XXJXX | RWK3044-12-88-E0XXX | RWK305-14-KL | RWK5420-13-89-E0XXT | FN5060-24-84 | FN5420-13-33-E2FXT | FN3288-20-33-C35-R65 | FN3287-20-33-C33-R65 | FN3288-20-33-C21-R65 | FN3288IT-20-33-C34-R65 | FN3120H-25-33 | FN3280H-25-33-69
6SL3210-1KE21-3AF1 | SINAMICS G120C PN 5.5KW | FN3440-6-112-E2XXJRX | FN3450-6-112-E2XXJRX | FN3442-6-112-E2XXJRX | FN3452-8-112-E2XXJRX | FN3446-6-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-10-44-E2XXJXX | FN3458-8-44-E2XXJXX | RWK3044-12-88-E0XXX | RWK305-14-KL | RWK5420-18-89-E0XXT | FN5060-24-84 | FN5420-18-33-E2FXT | FN3440-6-112-E2XXJRX | FN3450-6-112-E2XXJRX | FN3442-6-112-E2XXJRX | FN3452-8-112-E2XXJRX | FN3446-6-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-10-44-E2XXJXX | FN3458-8-44-E2XXJXX | RWK3044-12-88-E0XXX | RWK305-14-KL | RWK5420-13-89-E0XXT | FN5060-24-84 | FN5420-13-33-E2FXT | FN3288-20-33-C35-R65 | FN3287-20-33-C33-R65 | FN3288-20-33-C21-R65 | FN3288IT-20-33-C34-R65 | FN3120H-25-33 | FN3280H-25-33-69
6SL3210-1KE21-7UB1 | SINAMICS G120C USS/MB 7.5KW | FN3440-8-112-E2XXJRX | FN3450-8-112-E2XXJRX | FN3442-12-112-E2XXJRX | FN3452-10-112-E2XXJRX | FN3446-8-44-E2XXJXX | FN3446-6-44-E2XXJXX | FN3458-15-33-E2FAJXX | FN3458-10-44-E2XXJXX | RWK3044-18-89-E0XXX | RWK305-24-KL | RWK5420-18-89-E0XXT | FN5060-24-84 | FN5420-18-33-E2FXT | FN3440-8-112-E2XXJRX | FN3450-8-112-E2XXJRX | FN3442-12-112-E2XXJRX | FN3452-10-112-E2XXJRX | FN3446-8-44-E2XXJXX | FN3446-6-44-E2XXJXX | FN3458-15-33-E2FAJXX | FN3458-10-44-E2XXJXX | RWK3044-18-89-E0XXX | RWK305-24-KL | RWK5420-26-92-E0XXT | FN5060-24-84 | FN5420-26-33-E2FXT | FN3288-25-33-C35-R65 | FN3287-25-33-C33-R65 | FN3288-25-33-C21-R65 | FN3288IT-25-33-C34-R65 | FN3120H-25-33 | FN3280H-25-33-69
6SL3210-1KE21-7UP1 | SINAMICS G120C DP 7.5KW | FN3440-8-112-E2XXJRX | FN3450-8-112-E2XXJRX | FN3442-12-112-E2XXJRX | FN3452-10-112-E2XXJRX | FN3446-8-44-E2XXJXX | FN3446-6-44-E2XXJXX | FN3458-15-33-E2FAJXX | FN3458-10-44-E2XXJXX | RWK3044-18-89-E0XXX | RWK305-24-KL | RWK5420-18-89-E0XXT | FN5060-24-84 | FN5420-18-33-E2FXT | FN3440-8-112-E2XXJRX | FN3450-8-112-E2XXJRX | FN3442-12-112-E2XXJRX | FN3452-10-112-E2XXJRX | FN3446-8-44-E2XXJXX | FN3446-6-44-E2XXJXX | FN3458-15-33-E2FAJXX | FN3458-10-44-E2XXJXX | RWK3044-18-89-E0XXX | RWK305-24-KL | RWK5420-26-92-E0XXT | FN5060-24-84 | FN5420-26-33-E2FXT | FN3288-25-33-C35-R65 | FN3287-25-33-C33-R65 | FN3288-25-33-C21-R65 | FN3288IT-25-33-C34-R65 | FN3120H-25-33 | FN3280H-25-33-69
6SL3210-1KE21-7UF1 | SINAMICS G120C PN 7.5KW UNFIL SINAMICS G120C RATED POWER 7.5KW WITH 150% OVERLOAD FOR 3 SEC 3AC380-480V +10/-20% 47-63HZ UNFILTERED I/O-INTERFACE: 6DI. 2DO.1AI.1AO SAFE TORQUE OFF INTEGRATED FIELDBUS: PROFINET-PN PROTECTION: IP20/ UL OPEN TYPE SIZE: FSB 196x 100x 225.4 (HXWXD) EXTERNAL 24V | FN3440-8-112-E2XXJRX | FN3450-8-112-E2XXJRX | FN3442-12-112-E2XXJRX | FN3452-10-112-E2XXJRX | FN3446-8-44-E2XXJXX | FN3446-6-44-E2XXJXX | FN3458-15-33-E2FAJXX | FN3458-10-44-E2XXJXX | RWK3044-18-89-E0XXX | RWK305-24-KL | RWK5420-18-89-E0XXT | FN5060-24-84 | FN5420-18-33-E2FXT | FN3440-8-112-E2XXJRX | FN3450-8-112-E2XXJRX | FN3442-12-112-E2XXJRX | FN3452-10-112-E2XXJRX | FN3446-8-44-E2XXJXX | FN3446-6-44-E2XXJXX | FN3458-15-33-E2FAJXX | FN3458-10-44-E2XXJXX | RWK3044-18-89-E0XXX | RWK305-24-KL | RWK5420-26-92-E0XXT | FN5060-24-84 | FN5420-26-33-E2FXT | FN3288-25-33-C35-R65 | FN3287-25-33-C33-R65 | FN3288-25-33-C21-R65 | FN3288IT-25-33-C34-R65 | FN3120H-25-33 | FN3280H-25-33-69
6SL3210-1KE21-7AB1 | SINAMICS G120C USS/MB 7.5KW FILA SINAMICS G120C RATED POWER 7.5KW WITH 150% OVERLOAD FOR 3 SEC 3AC380-480V +10/-20% 47-63HZ INTEGRATED FILTER CLASS A I/O-INTERFACE: 6DI. 2DO.1AI.1AO SAFE TORQUE OFF INTEGRATED FIELDBUS: USS/ MODBUS RTU PROTECTION: IP20/ UL OPEN TYPE SIZE: FSB 196X100X203(HXWXD) EXTERNAL 24V | FN3440-8-112-E2XXJRX | FN3450-8-112-E2XXJRX | FN3442-12-112-E2XXJRX | FN3452-10-112-E2XXJRX | FN3446-8-44-E2XXJXX | FN3446-6-44-E2XXJXX | FN3458-15-33-E2FAJXX | FN3458-10-44-E2XXJXX | RWK3044-18-89-E0XXX | RWK305-24-KL | RWK5420-18-89-E0XXT | FN5060-24-84 | FN5420-18-33-E2FXT | FN3440-8-112-E2XXJRX | FN3450-8-112-E2XXJRX | FN3442-12-112-E2XXJRX | FN3452-10-112-E2XXJRX | FN3446-8-44-E2XXJXX | FN3446-6-44-E2XXJXX | FN3458-15-33-E2FAJXX | FN3458-10-44-E2XXJXX | RWK3044-18-89-E0XXX | RWK305-24-KL | RWK5420-26-92-E0XXT | FN5060-24-84 | FN5420-26-33-E2FXT | FN3288-25-33-C35-R65 | FN3287-25-33-C33-R65 | FN3288-25-33-C21-R65 | FN3288IT-25-33-C34-R65 | FN3120H-25-33 | FN3280H-25-33-69
6SL3210-1KE21-7AP1 | SINAMICS G120C DP 7.5KW FILA SINAMICS G120C RATED POWER 7.5KW WITH 150% OVERLOAD FOR 3 SEC 3AC380-480V +10/-20% 47-63HZ INTEGRATED FILTER CLASS A I/O-INTERFACE: 6DI. 2DO.1AI.1AO SAFE TORQUE OFF INTEGRATED FIELDBUS: PROFIBUS-DP PROTECTION: IP20/ UL OPEN TYPE SIZE: FSB 196X100X203(HXWXD) EXTERNAL 24V | FN3440-8-112-E2XXJRX | FN3450-8-112-E2XXJRX | FN3442-12-112-E2XXJRX | FN3452-10-112-E2XXJRX | FN3446-8-44-E2XXJXX | FN3446-6-44-E2XXJXX | FN3458-15-33-E2FAJXX | FN3458-10-44-E2XXJXX | RWK3044-18-89-E0XXX | RWK305-24-KL | RWK5420-18-89-E0XXT | FN5060-24-84 | FN5420-18-33-E2FXT | FN3440-8-112-E2XXJRX | FN3450-8-112-E2XXJRX | FN3442-12-112-E2XXJRX | FN3452-10-112-E2XXJRX | FN3446-8-44-E2XXJXX | FN3446-6-44-E2XXJXX | FN3458-15-33-E2FAJXX | FN3458-10-44-E2XXJXX | RWK3044-18-89-E0XXX | RWK305-24-KL | RWK5420-26-92-E0XXT | FN5060-24-84 | FN5420-26-33-E2FXT | FN3288-25-33-C35-R65 | FN3287-25-33-C33-R65 | FN3288-25-33-C21-R65 | FN3288IT-25-33-C34-R65 | FN3120H-25-33 | FN3280H-25-33-69
6SL3210-1KE21-7AF1 | SINAMICS G120C PN 7.5KW FILA SINAMICS G120C RATED POWER 7.5KW WITH 150% OVERLOAD FOR 3 SEC 3AC380-480V +10/-20% 47-63HZ INTEGRATED FILTER CLASS A I/O-INTERFACE: 6DI. 2DO.1AI.1AO SAFE TORQUE OFF INTEGRATED FIELDBUS: PROFINET-PN PROTECTION: IP20/ UL OPEN TYPE SIZE: FSB 196x 100x 225.4 (HXWXD) EXTERNAL 24V | FN3440-8-112-E2XXJRX | FN3450-8-112-E2XXJRX | FN3442-12-112-E2XXJRX | FN3452-10-112-E2XXJRX | FN3446-8-44-E2XXJXX | FN3446-6-44-E2XXJXX | FN3458-15-33-E2FAJXX | FN3458-10-44-E2XXJXX | RWK3044-18-89-E0XXX | RWK305-24-KL | RWK5420-18-89-E0XXT | FN5060-24-84 | FN5420-18-33-E2FXT | FN3440-8-112-E2XXJRX | FN3450-8-112-E2XXJRX | FN3442-12-112-E2XXJRX | FN3452-10-112-E2XXJRX | FN3446-8-44-E2XXJXX | FN3446-6-44-E2XXJXX | FN3458-15-33-E2FAJXX | FN3458-10-44-E2XXJXX | RWK3044-18-89-E0XXX | RWK305-24-KL | RWK5420-26-92-E0XXT | FN5060-24-84 | FN5420-26-33-E2FXT | FN3288-25-33-C35-R65 | FN3287-25-33-C33-R65 | FN3288-25-33-C21-R65 | FN3288IT-25-33-C34-R65 | FN3120H-25-33 | FN3280H-25-33-69
6SL3210-1KE22-6UB1 | SINAMICS G120C USS/MB 11.0KW | FN3440-11-113-E2FAJRX | FN3450-15-113-E2FAJRX | FN3442-16-113-E2FAJRX | FN3452-15-112-E2XXJRX | FN3446-11-33-E2FAJXX | FN3446-11-33-E2FAJXX | FN3458-20-33-E2FAJXX | FN3458-15-33-E2FAJXX | RWK3044-24-89-E0XXX | RWK305-32-KL | RWK5420-32-92-E0XXT | FN5060-30-99 | FN5420-32-33-E2FXT | FN3440-11-113-E2FAJRX | FN3450-15-113-E2FAJRX | FN3442-12-112-E2XXJRX | FN3452-15-112-E2XXJRX | FN3446-11-33-E2FAJXX | FN3446-8-44-E2XXJXX | FN3458-15-33-E2FAJXX | FN3458-15-33-E2FAJXX | RWK3044-24-89-E0XXX | RWK305-32-KL | RWK5420-26-92-E0XXT | FN5060-30-99 | FN5420-26-33-E2FXT | FN3288-40-33-C35-R65 | FN3287-40-33-C33-R65 | FN3288-40-33-C21-R65 | FN3288IT-40-33-C34-R65 | FN3120H-50-53 | FN3280H-36-33-69
6SL3210-1KE22-6UP1 | SINAMICS G120C DP 11.0KW | FN3440-11-113-E2FAJRX | FN3450-15-113-E2FAJRX | FN3442-16-113-E2FAJRX | FN3452-15-112-E2XXJRX | FN3446-11-33-E2FAJXX | FN3446-11-33-E2FAJXX | FN3458-20-33-E2FAJXX | FN3458-15-33-E2FAJXX | RWK3044-24-89-E0XXX | RWK305-32-KL | RWK5420-32-92-E0XXT | FN5060-30-99 | FN5420-32-33-E2FXT | FN3440-11-113-E2FAJRX | FN3450-15-113-E2FAJRX | FN3442-12-112-E2XXJRX | FN3452-15-112-E2XXJRX | FN3446-11-33-E2FAJXX | FN3446-8-44-E2XXJXX | FN3458-15-33-E2FAJXX | FN3458-15-33-E2FAJXX | RWK3044-24-89-E0XXX | RWK305-32-KL | RWK5420-26-92-E0XXT | FN5060-30-99 | FN5420-26-33-E2FXT | FN3288-40-33-C35-R65 | FN3287-40-33-C33-R65 | FN3288-40-33-C21-R65 | FN3288IT-40-33-C34-R65 | FN3120H-50-53 | FN3280H-36-33-69
6SL3210-1KE22-6UF1 | SINAMICS G120C PN 11.0KW | FN3440-11-113-E2FAJRX | FN3450-15-113-E2FAJRX | FN3442-16-113-E2FAJRX | FN3452-15-112-E2XXJRX | FN3446-11-33-E2FAJXX | FN3446-11-33-E2FAJXX | FN3458-20-33-E2FAJXX | FN3458-15-33-E2FAJXX | RWK3044-24-89-E0XXX | RWK305-32-KL | RWK5420-32-92-E0XXT | FN5060-30-99 | FN5420-32-33-E2FXT | FN3440-11-113-E2FAJRX | FN3450-15-113-E2FAJRX | FN3442-12-112-E2XXJRX | FN3452-15-112-E2XXJRX | FN3446-11-33-E2FAJXX | FN3446-8-44-E2XXJXX | FN3458-15-33-E2FAJXX | FN3458-15-33-E2FAJXX | RWK3044-24-89-E0XXX | RWK305-32-KL | RWK5420-26-92-E0XXT | FN5060-30-99 | FN5420-26-33-E2FXT | FN3288-40-33-C35-R65 | FN3287-40-33-C33-R65 | FN3288-40-33-C21-R65 | FN3288IT-40-33-C34-R65 | FN3120H-50-53 | FN3280H-36-33-69
6SL3210-1KE22-6AB1 | SINAMICS G120C USS/MB 11.0KW | FN3440-11-113-E2FAJRX | FN3450-15-113-E2FAJRX | FN3442-16-113-E2FAJRX | FN3452-15-112-E2XXJRX | FN3446-11-33-E2FAJXX | FN3446-11-33-E2FAJXX | FN3458-20-33-E2FAJXX | FN3458-15-33-E2FAJXX | RWK3044-24-89-E0XXX | RWK305-32-KL | RWK5420-32-92-E0XXT | FN5060-30-99 | FN5420-32-33-E2FXT | FN3440-11-113-E2FAJRX | FN3450-15-113-E2FAJRX | FN3442-12-112-E2XXJRX | FN3452-15-112-E2XXJRX | FN3446-11-33-E2FAJXX | FN3446-8-44-E2XXJXX | FN3458-15-33-E2FAJXX | FN3458-15-33-E2FAJXX | RWK3044-24-89-E0XXX | RWK305-32-KL | RWK5420-26-92-E0XXT | FN5060-30-99 | FN5420-26-33-E2FXT | FN3288-40-33-C35-R65 | FN3287-40-33-C33-R65 | FN3288-40-33-C21-R65 | FN3288IT-40-33-C34-R65 | FN3120H-50-53 | FN3280H-36-33-69
6SL3210-1KE22-6AP1 | SINAMICS G120C DP 11.0KW | FN3440-11-113-E2FAJRX | FN3450-15-113-E2FAJRX | FN3442-16-113-E2FAJRX | FN3452-15-112-E2XXJRX | FN3446-11-33-E2FAJXX | FN3446-11-33-E2FAJXX | FN3458-20-33-E2FAJXX | FN3458-15-33-E2FAJXX | RWK3044-24-89-E0XXX | RWK305-32-KL | RWK5420-32-92-E0XXT | FN5060-30-99 | FN5420-32-33-E2FXT | FN3440-11-113-E2FAJRX | FN3450-15-113-E2FAJRX | FN3442-12-112-E2XXJRX | FN3452-15-112-E2XXJRX | FN3446-11-33-E2FAJXX | FN3446-8-44-E2XXJXX | FN3458-15-33-E2FAJXX | FN3458-15-33-E2FAJXX | RWK3044-24-89-E0XXX | RWK305-32-KL | RWK5420-26-92-E0XXT | FN5060-30-99 | FN5420-26-33-E2FXT | FN3288-40-33-C35-R65 | FN3287-40-33-C33-R65 | FN3288-40-33-C21-R65 | FN3288IT-40-33-C34-R65 | FN3120H-50-53 | FN3280H-36-33-69
6SL3210-1KE22-6AF1 | SINAMICS G120C PN 11.0KW | FN3440-11-113-E2FAJRX | FN3450-15-113-E2FAJRX | FN3442-16-113-E2FAJRX | FN3452-15-112-E2XXJRX | FN3446-11-33-E2FAJXX | FN3446-11-33-E2FAJXX | FN3458-20-33-E2FAJXX | FN3458-15-33-E2FAJXX | RWK3044-24-89-E0XXX | RWK305-32-KL | RWK5420-32-92-E0XXT | FN5060-30-99 | FN5420-32-33-E2FXT | FN3440-11-113-E2FAJRX | FN3450-15-113-E2FAJRX | FN3442-12-112-E2XXJRX | FN3452-15-112-E2XXJRX | FN3446-11-33-E2FAJXX | FN3446-8-44-E2XXJXX | FN3458-15-33-E2FAJXX | FN3458-15-33-E2FAJXX | RWK3044-24-89-E0XXX | RWK305-32-KL | RWK5420-26-92-E0XXT | FN5060-30-99 | FN5420-26-33-E2FXT | FN3288-40-33-C35-R65 | FN3287-40-33-C33-R65 | FN3288-40-33-C21-R65 | FN3288IT-40-33-C34-R65 | FN3120H-50-53 | FN3280H-36-33-69
6SL3210-1KE23-2UB1 | SINAMICS G120C USS/MB 15.0KW | FN3440-15-113-E2FAJRX | FN3450-19-113-E2FAJRX | FN3442-20-113-E2FAJRX | FN3452-20-113-E2FAJRX | FN3446-15-33-E2FAJXX | FN3446-11-33-E2FAJXX | FN3458-25-33-E2FAJXX | FN3458-20-33-E2FAJXX | RWK3044-30-92-E0XXX | RWK305-45-KL | RWK5420-38-92-E0XXT | FN5060-45-99 | FN5420-38-33-E2FXT | FN3440-15-113-E2FAJRX | FN3450-19-113-E2FAJRX | FN3442-20-113-E2FAJRX | FN3452-20-113-E2FAJRX | FN3446-15-33-E2FAJXX | FN3446-11-33-E2FAJXX | FN3458-25-33-E2FAJXX | FN3458-20-33-E2FAJXX | RWK3044-30-92-E0XXX | RWK305-45-KL | RWK5420-38-92-E0XXT | FN5060-45-99 | FN5420-38-33-E2FXT | FN3288-50-53-C35-R65 | FN3287-50-53-C33-R65 | FN3288-50-53-C21-R65 | FN3288IT-50-53-C34-R65 | FN3120H-50-53 | FN3280H-64-34-69
6SL3210-1KE23-2UP1 | SINAMICS G120C DP 15.0KW | FN3440-15-113-E2FAJRX | FN3450-19-113-E2FAJRX | FN3442-20-113-E2FAJRX | FN3452-20-113-E2FAJRX | FN3446-15-33-E2FAJXX | FN3446-11-33-E2FAJXX | FN3458-25-33-E2FAJXX | FN3458-20-33-E2FAJXX | RWK3044-30-92-E0XXX | RWK305-45-KL | RWK5420-38-92-E0XXT | FN5060-45-99 | FN5420-38-33-E2FXT | FN3440-15-113-E2FAJRX | FN3450-19-113-E2FAJRX | FN3442-20-113-E2FAJRX | FN3452-20-113-E2FAJRX | FN3446-15-33-E2FAJXX | FN3446-11-33-E2FAJXX | FN3458-25-33-E2FAJXX | FN3458-20-33-E2FAJXX | RWK3044-30-92-E0XXX | RWK305-45-KL | RWK5420-38-92-E0XXT | FN5060-45-99 | FN5420-38-33-E2FXT | FN3288-50-53-C35-R65 | FN3287-50-53-C33-R65 | FN3288-50-53-C21-R65 | FN3288IT-50-53-C34-R65 | FN3120H-50-53 | FN3280H-64-34-69
6SL3210-1KE23-2UF1 | SINAMICS G120C PN 15.0KW | FN3440-15-113-E2FAJRX | FN3450-19-113-E2FAJRX | FN3442-20-113-E2FAJRX | FN3452-20-113-E2FAJRX | FN3446-15-33-E2FAJXX | FN3446-11-33-E2FAJXX | FN3458-25-33-E2FAJXX | FN3458-20-33-E2FAJXX | RWK3044-30-92-E0XXX | RWK305-45-KL | RWK5420-38-92-E0XXT | FN5060-45-99 | FN5420-38-33-E2FXT | FN3440-15-113-E2FAJRX | FN3450-19-113-E2FAJRX | FN3442-20-113-E2FAJRX | FN3452-20-113-E2FAJRX | FN3446-15-33-E2FAJXX | FN3446-11-33-E2FAJXX | FN3458-25-33-E2FAJXX | FN3458-20-33-E2FAJXX | RWK3044-30-92-E0XXX | RWK305-45-KL | RWK5420-38-92-E0XXT | FN5060-45-99 | FN5420-38-33-E2FXT | FN3288-50-53-C35-R65 | FN3287-50-53-C33-R65 | FN3288-50-53-C21-R65 | FN3288IT-50-53-C34-R65 | FN3120H-50-53 | FN3280H-64-34-69
6SL3210-1KE23-2AB1 | SINAMICS G120C USS/MB 15.0KW | FN3440-15-113-E2FAJRX | FN3450-19-113-E2FAJRX | FN3442-20-113-E2FAJRX | FN3452-20-113-E2FAJRX | FN3446-15-33-E2FAJXX | FN3446-11-33-E2FAJXX | FN3458-25-33-E2FAJXX | FN3458-20-33-E2FAJXX | RWK3044-30-92-E0XXX | RWK305-45-KL | RWK5420-38-92-E0XXT | FN5060-45-99 | FN5420-38-33-E2FXT | FN3440-15-113-E2FAJRX | FN3450-19-113-E2FAJRX | FN3442-20-113-E2FAJRX | FN3452-20-113-E2FAJRX | FN3446-15-33-E2FAJXX | FN3446-11-33-E2FAJXX | FN3458-25-33-E2FAJXX | FN3458-20-33-E2FAJXX | RWK3044-30-92-E0XXX | RWK305-45-KL | RWK5420-38-92-E0XXT | FN5060-45-99 | FN5420-38-33-E2FXT | FN3288-50-53-C35-R65 | FN3287-50-53-C33-R65 | FN3288-50-53-C21-R65 | FN3288IT-50-53-C34-R65 | FN3120H-50-53 | FN3280H-64-34-69
6SL3210-1KE23-2AP1 | SINAMICS G120C DP 15.0KW | FN3440-15-113-E2FAJRX | FN3450-19-113-E2FAJRX | FN3442-20-113-E2FAJRX | FN3452-20-113-E2FAJRX | FN3446-15-33-E2FAJXX | FN3446-11-33-E2FAJXX | FN3458-25-33-E2FAJXX | FN3458-20-33-E2FAJXX | RWK3044-30-92-E0XXX | RWK305-45-KL | RWK5420-38-92-E0XXT | FN5060-45-99 | FN5420-38-33-E2FXT | FN3440-15-113-E2FAJRX | FN3450-19-113-E2FAJRX | FN3442-20-113-E2FAJRX | FN3452-20-113-E2FAJRX | FN3446-15-33-E2FAJXX | FN3446-11-33-E2FAJXX | FN3458-25-33-E2FAJXX | FN3458-20-33-E2FAJXX | RWK3044-30-92-E0XXX | RWK305-45-KL | RWK5420-38-92-E0XXT | FN5060-45-99 | FN5420-38-33-E2FXT | FN3288-50-53-C35-R65 | FN3287-50-53-C33-R65 | FN3288-50-53-C21-R65 | FN3288IT-50-53-C34-R65 | FN3120H-50-53 | FN3280H-64-34-69
6SL3210-1KE23-2AF1 | SINAMICS G120C PN 15.0KW | FN3440-15-113-E2FAJRX | FN3450-19-113-E2FAJRX | FN3442-20-113-E2FAJRX | FN3452-20-113-E2FAJRX | FN3446-15-33-E2FAJXX | FN3446-11-33-E2FAJXX | FN3458-25-33-E2FAJXX | FN3458-20-33-E2FAJXX | RWK3044-30-92-E0XXX | RWK305-45-KL | RWK5420-38-92-E0XXT | FN5060-45-99 | FN5420-38-33-E2FXT | FN3440-15-113-E2FAJRX | FN3450-19-113-E2FAJRX | FN3442-20-113-E2FAJRX | FN3452-20-113-E2FAJRX | FN3446-15-33-E2FAJXX | FN3446-11-33-E2FAJXX | FN3458-25-33-E2FAJXX | FN3458-20-33-E2FAJXX | RWK3044-30-92-E0XXX | RWK305-45-KL | RWK5420-38-92-E0XXT | FN5060-45-99 | FN5420-38-33-E2FXT | FN3288-50-53-C35-R65 | FN3287-50-53-C33-R65 | FN3288-50-53-C21-R65 | FN3288IT-50-53-C34-R65 | FN3120H-50-53 | FN3280H-64-34-69
6SL3210-1KE23-8UB1 | SINAMICS G120C USS/MB 18.5KW | FN3440-19-113-E2FAJRX | FN3450-19-113-E2FAJRX | FN3442-24-113-E2FAJRX | FN3452-25-113-E2FAJRX | FN3446-19-33-E2FAJXX | FN3446-15-33-E2FAJXX | FN3458-30-33-E2FAJXX | FN3458-25-33-E2FAJXX | RWK3044-48-92-E0XXX | RWK305-45-KL | RWK5420-45-92-E0XXT | FN5060-45-99 | FN5420-45-34-E2FXT | FN3440-22-115-E2FAJRX | FN3450-22-113-E2FAJRX | FN3442-24-113-E2FAJRX | FN3452-25-113-E2FAJRX | FN3446-19-33-E2FAJXX | FN3446-19-33-E2FAJXX | FN3458-30-33-E2FAJXX | FN3458-25-33-E2FAJXX | RWK3044-48-92-E0XXX | RWK305-60-KL | RWK5420-60-92-E0XXT | FN5060-60-99 | FN5420-60-34-E2FXT | FN3288-50-53-C35-R65 | FN3287-50-53-C33-R65 | FN3288-50-53-C21-R65 | FN3288IT-50-53-C34-R65 | FN3120H-50-53 | FN3280H-64-34-69
6SL3210-1KE23-8UP1 | SINAMICS G120C DP 18.5KW | FN3440-19-113-E2FAJRX | FN3450-19-113-E2FAJRX | FN3442-24-113-E2FAJRX | FN3452-25-113-E2FAJRX | FN3446-19-33-E2FAJXX | FN3446-15-33-E2FAJXX | FN3458-30-33-E2FAJXX | FN3458-25-33-E2FAJXX | RWK3044-48-92-E0XXX | RWK305-45-KL | RWK5420-45-92-E0XXT | FN5060-45-99 | FN5420-45-34-E2FXT | FN3440-22-115-E2FAJRX | FN3450-22-113-E2FAJRX | FN3442-24-113-E2FAJRX | FN3452-25-113-E2FAJRX | FN3446-19-33-E2FAJXX | FN3446-19-33-E2FAJXX | FN3458-30-33-E2FAJXX | FN3458-25-33-E2FAJXX | RWK3044-48-92-E0XXX | RWK305-60-KL | RWK5420-60-92-E0XXT | FN5060-60-99 | FN5420-60-34-E2FXT | FN3288-50-53-C35-R65 | FN3287-50-53-C33-R65 | FN3288-50-53-C21-R65 | FN3288IT-50-53-C34-R65 | FN3120H-50-53 | FN3280H-64-34-69
6SL3210-1KE23-8UF1 | SINAMICS G120C PN 18.5KW | FN3440-19-113-E2FAJRX | FN3450-19-113-E2FAJRX | FN3442-24-113-E2FAJRX | FN3452-25-113-E2FAJRX | FN3446-19-33-E2FAJXX | FN3446-15-33-E2FAJXX | FN3458-30-33-E2FAJXX | FN3458-25-33-E2FAJXX | RWK3044-48-92-E0XXX | RWK305-45-KL | RWK5420-45-92-E0XXT | FN5060-45-99 | FN5420-45-34-E2FXT | FN3440-22-115-E2FAJRX | FN3450-22-113-E2FAJRX | FN3442-24-113-E2FAJRX | FN3452-25-113-E2FAJRX | FN3446-19-33-E2FAJXX | FN3446-19-33-E2FAJXX | FN3458-30-33-E2FAJXX | FN3458-25-33-E2FAJXX | RWK3044-48-92-E0XXX | RWK305-60-KL | RWK5420-60-92-E0XXT | FN5060-60-99 | FN5420-60-34-E2FXT | FN3288-50-53-C35-R65 | FN3287-50-53-C33-R65 | FN3288-50-53-C21-R65 | FN3288IT-50-53-C34-R65 | FN3120H-50-53 | FN3280H-64-34-69
6SL3210-1KE23-8AB1 | SINAMICS G120C USS/MB 18.5KW | FN3440-19-113-E2FAJRX | FN3450-19-113-E2FAJRX | FN3442-24-113-E2FAJRX | FN3452-25-113-E2FAJRX | FN3446-19-33-E2FAJXX | FN3446-15-33-E2FAJXX | FN3458-30-33-E2FAJXX | FN3458-25-33-E2FAJXX | RWK3044-48-92-E0XXX | RWK305-45-KL | RWK5420-45-92-E0XXT | FN5060-45-99 | FN5420-45-34-E2FXT | FN3440-22-115-E2FAJRX | FN3450-22-113-E2FAJRX | FN3442-24-113-E2FAJRX | FN3452-25-113-E2FAJRX | FN3446-19-33-E2FAJXX | FN3446-19-33-E2FAJXX | FN3458-30-33-E2FAJXX | FN3458-25-33-E2FAJXX | RWK3044-48-92-E0XXX | RWK305-60-KL | RWK5420-60-92-E0XXT | FN5060-60-99 | FN5420-60-34-E2FXT | FN3288-50-53-C35-R65 | FN3287-50-53-C33-R65 | FN3288-50-53-C21-R65 | FN3288IT-50-53-C34-R65 | FN3120H-50-53 | FN3280H-64-34-69
6SL3210-1KE23-8AP1 | SINAMICS G120C DP 18.5KW | FN3440-19-113-E2FAJRX | FN3450-19-113-E2FAJRX | FN3442-24-113-E2FAJRX | FN3452-25-113-E2FAJRX | FN3446-19-33-E2FAJXX | FN3446-15-33-E2FAJXX | FN3458-30-33-E2FAJXX | FN3458-25-33-E2FAJXX | RWK3044-48-92-E0XXX | RWK305-45-KL | RWK5420-45-92-E0XXT | FN5060-45-99 | FN5420-45-34-E2FXT | FN3440-22-115-E2FAJRX | FN3450-22-113-E2FAJRX | FN3442-24-113-E2FAJRX | FN3452-25-113-E2FAJRX | FN3446-19-33-E2FAJXX | FN3446-19-33-E2FAJXX | FN3458-30-33-E2FAJXX | FN3458-25-33-E2FAJXX | RWK3044-48-92-E0XXX | RWK305-60-KL | RWK5420-60-92-E0XXT | FN5060-60-99 | FN5420-60-34-E2FXT | FN3288-50-53-C35-R65 | FN3287-50-53-C33-R65 | FN3288-50-53-C21-R65 | FN3288IT-50-53-C34-R65 | FN3120H-50-53 | FN3280H-64-34-69
6SL3210-1KE23-8AF1 | SINAMICS G120C PN 18.5KW | FN3440-19-113-E2FAJRX | FN3450-19-113-E2FAJRX | FN3442-24-113-E2FAJRX | FN3452-25-113-E2FAJRX | FN3446-19-33-E2FAJXX | FN3446-15-33-E2FAJXX | FN3458-30-33-E2FAJXX | FN3458-25-33-E2FAJXX | RWK3044-48-92-E0XXX | RWK305-45-KL | RWK5420-45-92-E0XXT | FN5060-45-99 | FN5420-45-34-E2FXT | FN3440-22-115-E2FAJRX | FN3450-22-113-E2FAJRX | FN3442-24-113-E2FAJRX | FN3452-25-113-E2FAJRX | FN3446-19-33-E2FAJXX | FN3446-19-33-E2FAJXX | FN3458-30-33-E2FAJXX | FN3458-25-33-E2FAJXX | RWK3044-48-92-E0XXX | RWK305-60-KL | RWK5420-60-92-E0XXT | FN5060-60-99 | FN5420-60-34-E2FXT | FN3288-50-53-C35-R65 | FN3287-50-53-C33-R65 | FN3288-50-53-C21-R65 | FN3288IT-50-53-C34-R65 | FN3120H-50-53 | FN3280H-64-34-69
6SL3210-1KE24-4UF1 |  | FN3440-22-115-E2FAJRX | FN3450-22-113-E2FAJRX | FN3442-24-113-E2FAJRX | FN3452-30-113-E2FAJRX | FN3446-22-33-E2FAJXX | FN3446-19-33-E2FAJXX | FN3458-40-34-E2FAJXX | FN3458-30-33-E2FAJXX | RWK3044-48-92-E0XXX | RWK305-60-KL | RWK5420-60-92-E0XXT | FN5060-60-99 | FN5420-60-34-E2FXT | FN3440-30-115-E2FAJRX | FN3450-30-115-E2FAJRX | FN3442-32-115-E2FAJRX | FN3452-30-113-E2FAJRX | FN3446-22-33-E2FAJXX | FN3446-19-33-E2FAJXX | FN3458-40-34-E2FAJXX | FN3458-30-33-E2FAJXX | RWK3044-59-92-E0XXX | RWK305-60-KL | RWK5420-60-92-E0XXT | FN5060-60-99 | FN5420-60-34-E2FXT | FN3288-50-53-C35-R65 | FN3287-50-53-C33-R65 | FN3288-50-53-C21-R65 | FN3288IT-50-53-C34-R65 | FN3120H-50-53 | FN3280H-64-34-69
6SL3210-1KE24-4AF1 |  | FN3440-22-115-E2FAJRX | FN3450-22-113-E2FAJRX | FN3442-24-113-E2FAJRX | FN3452-30-113-E2FAJRX | FN3446-22-33-E2FAJXX | FN3446-19-33-E2FAJXX | FN3458-40-34-E2FAJXX | FN3458-30-33-E2FAJXX | RWK3044-48-92-E0XXX | RWK305-60-KL | RWK5420-60-92-E0XXT | FN5060-60-99 | FN5420-60-34-E2FXT | FN3440-30-115-E2FAJRX | FN3450-30-115-E2FAJRX | FN3442-32-115-E2FAJRX | FN3452-30-113-E2FAJRX | FN3446-22-33-E2FAJXX | FN3446-19-33-E2FAJXX | FN3458-40-34-E2FAJXX | FN3458-30-33-E2FAJXX | RWK3044-59-92-E0XXX | RWK305-60-KL | RWK5420-60-92-E0XXT | FN5060-60-99 | FN5420-60-34-E2FXT | FN3288-50-53-C35-R65 | FN3287-50-53-C33-R65 | FN3288-50-53-C21-R65 | FN3288IT-50-53-C34-R65 | FN3120H-50-53 | FN3280H-64-34-69
6SL3210-1KE26-0UF1 |  | FN3440-30-115-E2FAJRX | FN3450-37-115-E2FAJRX | FN3442-40-115-E2FAJRX | FN3452-40-115-E2FAJRX | FN3446-30-34-E2FAJXX | FN3446-22-33-E2FAJXX | FN3458-50-34-E2FAJXX | FN3458-40-34-E2FAJXX | RWK3044-59-92-E0XXX | RWK305-72-KL | RWK5420-75-99-E0XXT | FN5060-70-99 | FN5420-75-35-E2FXT | FN3440-30-115-E2FAJRX | FN3450-37-115-E2FAJRX | FN3442-40-115-E2FAJRX | FN3452-40-115-E2FAJRX | FN3446-30-34-E2FAJXX | FN3446-22-33-E2FAJXX | FN3458-50-34-E2FAJXX | FN3458-40-34-E2FAJXX | RWK3044-59-92-E0XXX | RWK305-72-KL | RWK5420-75-99-E0XXT | FN5060-70-99 | FN5420-75-35-E2FXT | FN3288-63-53-C35-R65 | FN3287-63-53-C33-R65 | FN3288-63-53-C21-R65 | FN3288IT-63-53-C34-R65 | FN3120H-80-35 | FN3280H-64-34-69
6SL3210-1KE26-0AF1 |  | FN3440-30-115-E2FAJRX | FN3450-37-115-E2FAJRX | FN3442-40-115-E2FAJRX | FN3452-40-115-E2FAJRX | FN3446-30-34-E2FAJXX | FN3446-22-33-E2FAJXX | FN3458-50-34-E2FAJXX | FN3458-40-34-E2FAJXX | RWK3044-59-92-E0XXX | RWK305-72-KL | RWK5420-75-99-E0XXT | FN5060-70-99 | FN5420-75-35-E2FXT | FN3440-30-115-E2FAJRX | FN3450-37-115-E2FAJRX | FN3442-40-115-E2FAJRX | FN3452-40-115-E2FAJRX | FN3446-30-34-E2FAJXX | FN3446-22-33-E2FAJXX | FN3458-50-34-E2FAJXX | FN3458-40-34-E2FAJXX | RWK3044-59-92-E0XXX | RWK305-72-KL | RWK5420-75-99-E0XXT | FN5060-70-99 | FN5420-75-35-E2FXT | FN3288-63-53-C35-R65 | FN3287-63-53-C33-R65 | FN3288-63-53-C21-R65 | FN3288IT-63-53-C34-R65 | FN3120H-80-35 | FN3280H-64-34-69
6SL3210-1KE27-0UF1 |  | FN3440-37-115-E2FAJRX | FN3450-45-115-E2FAJRX | FN3442-48-115-E2FAJRX | FN3452-50-115-E2FAJRX | FN3446-37-34-E2FAJXX | FN3446-30-34-E2FAJXX | FN3458-60-35-E2FAJXX | FN3458-50-34-E2FAJXX | RWK3044-72-99-E0XXX | RWK305-90-KL | RWK5420-75-99-E0XXT | FN5060-90-99 | FN5420-75-35-E2FXT | FN3440-45-115-E2FAJRX | FN3450-45-115-E2FAJRX | FN3442-48-115-E2FAJRX | FN3452-60-115-E2FAJRX | FN3446-37-34-E2FAJXX | FN3446-30-34-E2FAJXX | FN3458-60-35-E2FAJXX | FN3458-50-34-E2FAJXX | RWK3044-88-99-E0XXX | RWK305-90-KL | RWK5420-90-99-E0XXT | FN5060-90-99 | FN5420-90-35-E2FXT | FN3288-80-34-C35-R65 | FN3287-80-34-C33-R65 | FN3288-80-34-C21-R65 | FN3288IT-80-34-C34-R65 | FN3120H-80-35 | FN3280H-64-34-69
6SL3210-1KE27-0AF1 |  | FN3440-37-115-E2FAJRX | FN3450-45-115-E2FAJRX | FN3442-48-115-E2FAJRX | FN3452-50-115-E2FAJRX | FN3446-37-34-E2FAJXX | FN3446-30-34-E2FAJXX | FN3458-60-35-E2FAJXX | FN3458-50-34-E2FAJXX | RWK3044-72-99-E0XXX | RWK305-90-KL | RWK5420-75-99-E0XXT | FN5060-90-99 | FN5420-75-35-E2FXT | FN3440-45-115-E2FAJRX | FN3450-45-115-E2FAJRX | FN3442-48-115-E2FAJRX | FN3452-60-115-E2FAJRX | FN3446-37-34-E2FAJXX | FN3446-30-34-E2FAJXX | FN3458-60-35-E2FAJXX | FN3458-50-34-E2FAJXX | RWK3044-88-99-E0XXX | RWK305-90-KL | RWK5420-90-99-E0XXT | FN5060-90-99 | FN5420-90-35-E2FXT | FN3288-80-34-C35-R65 | FN3287-80-34-C33-R65 | FN3288-80-34-C21-R65 | FN3288IT-80-34-C34-R65 | FN3120H-80-35 | FN3280H-64-34-69
6SL3210-1KE28-4UF1 |  | FN3440-45-115-E2FAJRX | FN3450-45-115-E2FAJRX | FN3442-60-115-E2FAJRX | FN3452-60-115-E2FAJRX | FN3446-45-35-E2FAJXX | FN3446-37-34-E2FAJXX | FN3458-75-35-E2FAJXX | FN3458-60-35-E2FAJXX | RWK3044-88-99-E0XXX | RWK305-90-KL | RWK5420-90-99-E0XXT | FN5060-90-99 | FN5420-90-35-E2FXT | FN3440-55-115-E2FAJRX | FN3450-55-115-E2FAJRX | FN3442-60-115-E2FAJRX | FN3452-60-115-E2FAJRX | FN3446-45-35-E2FAJXX | FN3446-45-35-E2FAJXX | FN3458-75-35-E2FAJXX | FN3458-75-35-E2FAJXX | RWK3044-120-99-E0XXX | RWK305-110-KL | RWK5420-110-99-E0XXT | FN5060-110-99 | FN5420-110-35-E2FXT | FN3288-100-35-C35-R65 | FN3287-100-35-C33-R65 | FN3288-100-35-C21-R65 | FN3288IT-100-35-C34-R65 | FN3120H-80-35 | FN3280H-80-35-69
6SL3210-1KE28-4AF1 |  | FN3440-45-115-E2FAJRX | FN3450-45-115-E2FAJRX | FN3442-60-115-E2FAJRX | FN3452-60-115-E2FAJRX | FN3446-45-35-E2FAJXX | FN3446-37-34-E2FAJXX | FN3458-75-35-E2FAJXX | FN3458-60-35-E2FAJXX | RWK3044-88-99-E0XXX | RWK305-90-KL | RWK5420-90-99-E0XXT | FN5060-90-99 | FN5420-90-35-E2FXT | FN3440-55-115-E2FAJRX | FN3450-55-115-E2FAJRX | FN3442-60-115-E2FAJRX | FN3452-60-115-E2FAJRX | FN3446-45-35-E2FAJXX | FN3446-45-35-E2FAJXX | FN3458-75-35-E2FAJXX | FN3458-75-35-E2FAJXX | RWK3044-120-99-E0XXX | RWK305-110-KL | RWK5420-110-99-E0XXT | FN5060-110-99 | FN5420-110-35-E2FXT | FN3288-100-35-C35-R65 | FN3287-100-35-C33-R65 | FN3288-100-35-C21-R65 | FN3288IT-100-35-C34-R65 | FN3120H-80-35 | FN3280H-80-35-69
6SL3210-1KE31-1UF1 |  | FN3440-55-115-E2FAJRX | FN3450-55-115-E2FAJRX | FN3442-80-115-E2FAJRX | FN3452-75-115-E2FAJRX | FN3446-55-35-E2FAJXX | FN3446-45-35-E2FAJXX | FN3458-100-40-E2FAJXX | FN3458-75-35-E2FAJXX | RWK3044-120-99-E0XXX | RWK305-124-KS | RWK5420-145-99-E0XXT | FN5060-150-99 | FN5420-145-99-E0XXT | FN3440-75-116-E2FAJRX | FN3450-75-115-E2FAJRX | FN3442-80-115-E2FAJRX | FN3452-75-115-E2FAJRX | FN3446-55-35-E2FAJXX | FN3446-55-35-E2FAJXX | FN3458-100-40-E2FAJXX | FN3458-100-40-E2FAJXX | RWK3044-120-99-E0XXX | RWK305-124-KS | RWK5420-145-99-E0XXT | FN5060-150-99 | FN5420-145-99-E0XXT | FN3288-100-35-C35-R65 | FN3287-100-35-C33-R65 | FN3288-100-35-C21-R65 | FN3288IT-100-35-C34-R65 | FN3120H-110-35 | FN3280H-120-35-69
6SL3210-1KE31-1AF1 |  | FN3440-55-115-E2FAJRX | FN3450-55-115-E2FAJRX | FN3442-80-115-E2FAJRX | FN3452-75-115-E2FAJRX | FN3446-55-35-E2FAJXX | FN3446-45-35-E2FAJXX | FN3458-100-40-E2FAJXX | FN3458-75-35-E2FAJXX | RWK3044-120-99-E0XXX | RWK305-124-KS | RWK5420-145-99-E0XXT | FN5060-150-99 | FN5420-145-99-E0XXT | FN3440-75-116-E2FAJRX | FN3450-75-115-E2FAJRX | FN3442-80-115-E2FAJRX | FN3452-75-115-E2FAJRX | FN3446-55-35-E2FAJXX | FN3446-55-35-E2FAJXX | FN3458-100-40-E2FAJXX | FN3458-100-40-E2FAJXX | RWK3044-120-99-E0XXX | RWK305-124-KS | RWK5420-145-99-E0XXT | FN5060-150-99 | FN5420-145-99-E0XXT | FN3288-100-35-C35-R65 | FN3287-100-35-C33-R65 | FN3288-100-35-C21-R65 | FN3288IT-100-35-C34-R65 | FN3120H-110-35 | FN3280H-120-35-69
6SL3210-1KE31-4UF1 |  | FN3440-75-116-E2FAJRX | FN3450-90-116-E2FAJRX | FN3442-100-116-E2FAJRX | FN3452-100-115-E2FAJRX | FN3446-75-40-E2FAJXX | FN3446-75-40-E2FAJXX | FN3458-125-40-E2FAJXX | FN3458-100-40-E2FAJXX | RWK3044-180-99-E0XXX | RWK305-156-KS | RWK5420-180-99-E0XXT | FN5060-150-99 | FN5420-180-99-E0XXT | FN3440-75-116-E2FAJRX | FN3450-90-116-E2FAJRX | FN3442-100-116-E2FAJRX | FN3452-100-115-E2FAJRX | FN3446-75-40-E2FAJXX | FN3446-75-40-E2FAJXX | FN3458-125-40-E2FAJXX | FN3458-100-40-E2FAJXX | RWK3044-180-99-E0XXX | RWK305-156-KS | RWK5420-180-99-E0XXT | FN5060-180-99 | FN5420-180-99-E0XXT | FN3288-160-40-C35-R65 | FN3287-160-40-C33-R65 | FN3288-160-40-C21-R65 | FN3288IT-160-40-C34-R65 | FN3120H-150-40 | FN3280H-160-40-69
6SL3210-1KE31-4AF1 |  | FN3440-75-116-E2FAJRX | FN3450-90-116-E2FAJRX | FN3442-100-116-E2FAJRX | FN3452-100-115-E2FAJRX | FN3446-75-40-E2FAJXX | FN3446-75-40-E2FAJXX | FN3458-125-40-E2FAJXX | FN3458-100-40-E2FAJXX | RWK3044-180-99-E0XXX | RWK305-156-KS | RWK5420-180-99-E0XXT | FN5060-150-99 | FN5420-180-99-E0XXT | FN3440-75-116-E2FAJRX | FN3450-90-116-E2FAJRX | FN3442-100-116-E2FAJRX | FN3452-100-115-E2FAJRX | FN3446-75-40-E2FAJXX | FN3446-75-40-E2FAJXX | FN3458-125-40-E2FAJXX | FN3458-100-40-E2FAJXX | RWK3044-180-99-E0XXX | RWK305-156-KS | RWK5420-180-99-E0XXT | FN5060-180-99 | FN5420-180-99-E0XXT | FN3288-160-40-C35-R65 | FN3287-160-40-C33-R65 | FN3288-160-40-C21-R65 | FN3288IT-160-40-C34-R65 | FN3120H-150-40 | FN3280H-160-40-69
6SL3210-1KE31-7UF1 |  | FN3440-90-116-E2FAJRX | FN3450-90-116-E2FAJRX | FN3442-120-116-E2FAJRX | FN3452-125-116-E2FAJRX | FN3446-90-40-E2FAJXX | FN3446-75-40-E2FAJXX | FN3458-150-40-E2FAJXX | FN3458-125-40-E2FAJXX | RWK3044-180-99-E0XXX | RWK305-182-KS | RWK5420-180-99-E0XXT | FN5060-180-99 | FN5420-180-99-E0XXT | FN3440-110-118-E2FAJRX | FN3450-110-116-E2FAJRX | FN3442-120-116-E2FAJRX | FN3452-150-116-E2FAJRX | FN3446-110-40-E2FAJXX | FN3446-90-40-E2FAJXX | FN3458-200-99-E2FAJXX | FN3458-150-40-E2FAJXX | RWK3044-210-99-E0XXX | RWK305-230-KS | RWK5420-200-99-E0XXT | FN5060-250-99 | FN5420-200-99-E0XXT | FN3288-160-40-C35-R65 | FN3287-160-40-C33-R65 | FN3288-160-40-C21-R65 | FN3288IT-160-40-C34-R65 | FN3120H-230-40 | FN3280H-160-40-69
6SL3210-1KE31-7AF1 |  | FN3440-90-116-E2FAJRX | FN3450-90-116-E2FAJRX | FN3442-120-116-E2FAJRX | FN3452-125-116-E2FAJRX | FN3446-90-40-E2FAJXX | FN3446-75-40-E2FAJXX | FN3458-150-40-E2FAJXX | FN3458-125-40-E2FAJXX | RWK3044-180-99-E0XXX | RWK305-182-KS | RWK5420-180-99-E0XXT | FN5060-180-99 | FN5420-180-99-E0XXT | FN3440-110-118-E2FAJRX | FN3450-110-116-E2FAJRX | FN3442-120-116-E2FAJRX | FN3452-150-116-E2FAJRX | FN3446-110-40-E2FAJXX | FN3446-90-40-E2FAJXX | FN3458-200-99-E2FAJXX | FN3458-150-40-E2FAJXX | RWK3044-210-99-E0XXX | RWK305-230-KS | RWK5420-200-99-E0XXT | FN5060-250-99 | FN5420-200-99-E0XXT | FN3288-160-40-C35-R65 | FN3287-160-40-C33-R65 | FN3288-160-40-C21-R65 | FN3288IT-160-40-C34-R65 | FN3120H-230-40 | FN3280H-160-40-69
6SL3210-1KE32-1UF1 |  | FN3440-132-118-E2FAJXX | FN3450-110-116-E2FAJRX | FN3442-160-118-E2FAJRX | FN3452-150-116-E2FAJRX | FN3446-110-40-E2FAJXX | FN3446-90-40-E2FAJXX | FN3458-200-99-E2FAJXX | FN3458-150-40-E2FAJXX | RWK3044-260-99-E0XXX | RWK305-230-KS | RWK5420-250-99-E0XXT | FN5060-250-99 | FN5420-250-99-E0XXT | FN3440-132-118-E2FAJXX | FN3450-132-118-E2FAJRX | FN3442-160-118-E2FAJRX | FN3452-150-116-E2FAJRX | FN3446-132-99-E2FAJXX | FN3446-110-40-E2FAJXX | FN3458-200-99-E2FAJXX | FN3458-200-99-E2FAJXX | RWK3044-260-99-E0XXX | RWK305-280-KS | RWK5420-250-99-E0XXT | FN5060-250-99 | FN5420-250-99-E0XXT | FN3288-230-40-C35-R65 | FN3287-230-40-C33-R65 | FN3288-230-40-C21-R65 | FN3288IT-230-40-C34-R65 | FN3120H-230-40 | FN3280H-200-40-69
6SL3210-1KE32-1AF1 |  | FN3440-132-118-E2FAJXX | FN3450-110-116-E2FAJRX | FN3442-160-118-E2FAJRX | FN3452-150-116-E2FAJRX | FN3446-110-40-E2FAJXX | FN3446-90-40-E2FAJXX | FN3458-200-99-E2FAJXX | FN3458-150-40-E2FAJXX | RWK3044-260-99-E0XXX | RWK305-230-KS | RWK5420-250-99-E0XXT | FN5060-250-99 | FN5420-250-99-E0XXT | FN3440-132-118-E2FAJXX | FN3450-132-118-E2FAJRX | FN3442-160-118-E2FAJRX | FN3452-150-116-E2FAJRX | FN3446-132-99-E2FAJXX | FN3446-110-40-E2FAJXX | FN3458-200-99-E2FAJXX | FN3458-200-99-E2FAJXX | RWK3044-260-99-E0XXX | RWK305-280-KS | RWK5420-250-99-E0XXT | FN5060-250-99 | FN5420-250-99-E0XXT | FN3288-230-40-C35-R65 | FN3287-230-40-C33-R65 | FN3288-230-40-C21-R65 | FN3288IT-230-40-C34-R65 | FN3120H-230-40 | FN3280H-200-40-69
6SL3210-1KE32-4UF1 |  | FN3440-132-118-E2FAJXX | FN3450-160-118-E2FAJXX | FN3442-200-118-E2FAJXX | FN3452-200-118-E2FAJRX | FN3446-132-99-E2FAJXX | FN3446-110-40-E2FAJXX | FN3458-250-99-E2FAJXX | FN3458-200-99-E2FAJXX | RWK3044-320-99-E0XXX | RWK305-280-KS | RWK5420-300-99-E0XXT | FN5060-320-99 | FN5420-300-99-E0XXT | FN3440-160-118-E2FAJXX | FN3450-160-118-E2FAJXX | FN3442-200-118-E2FAJXX | FN3452-250-118-E2FAJXX | FN3446-160-99-E2FAJXX | FN3446-132-99-E2FAJXX | FN3458-250-99-E2FAJXX | FN3458-200-99-E2FAJXX | RWK3044-320-99-E0XXX | RWK305-330-KS | RWK5420-300-99-E0XXT | FN5060-320-99 | FN5420-300-99-E0XXT | FN3288-230-40-C35-R65 | FN3287-230-40-C33-R65 | FN3288-230-40-C21-R65 | FN3288IT-230-40-C34-R65 | FN3120H-230-40 | FN3280H-300-99-69
6SL3210-1KE32-4AF1 |  | FN3440-132-118-E2FAJXX | FN3450-160-118-E2FAJXX | FN3442-200-118-E2FAJXX | FN3452-200-118-E2FAJRX | FN3446-132-99-E2FAJXX | FN3446-110-40-E2FAJXX | FN3458-250-99-E2FAJXX | FN3458-200-99-E2FAJXX | RWK3044-320-99-E0XXX | RWK305-280-KS | RWK5420-300-99-E0XXT | FN5060-320-99 | FN5420-300-99-E0XXT | FN3440-160-118-E2FAJXX | FN3450-160-118-E2FAJXX | FN3442-200-118-E2FAJXX | FN3452-250-118-E2FAJXX | FN3446-160-99-E2FAJXX | FN3446-132-99-E2FAJXX | FN3458-250-99-E2FAJXX | FN3458-200-99-E2FAJXX | RWK3044-320-99-E0XXX | RWK305-330-KS | RWK5420-300-99-E0XXT | FN5060-320-99 | FN5420-300-99-E0XXT | FN3288-230-40-C35-R65 | FN3287-230-40-C33-R65 | FN3288-230-40-C21-R65 | FN3288IT-230-40-C34-R65 | FN3120H-230-40 | FN3280H-300-99-69

## G120X 200VAC-240VAC
|  | Drive in Low overload (LO) | [5 empty] | Drive in High overload (HO)
G120X 200VAC-240VAC | Power Modul Description | PHF 200-240V 50Hz LO | PHF 200-240V 60Hz LO | dv/dt Reactor 0.8% LO | dv/dt Reactor 6% LO | dv/dt Filter LO | SineWave Filter LO | PHF 200V 50Hz HO | PHF 240V 60Hz HO | dv/dt Reactor 0.8% HO | dv/dt Reactor 6% HO | dv/dt Filter HO | SineWave Filter HO | EMC Filter Motor Cable Lenght ≤ 50m Class C1 | EMC Filter Motor Cable Lenght ≤ 50m Class C2 | EMC Filter Low Leakage Current Motor Cable Lenght ≤ 35m Class C2 | EMC Filter for IT Power Networks Class C2 | EMC Filter Motor Cable Lenght > 50m Class C1 | EMC Filter 3-Phase with Neutral for Machine Tools and Low Leakage Current Applications
6SL32x0-xYC10-xUx0 | SINAMICS G120X Rated power: 0.75 kW | FN3416LV-10-44 | FN3418LV-8-44 | RWK305-7.8-KL | RWK5420-5.9-88-E0XXT | FN5060-12-84 | FN5420-5.9-44-E2FXT | FN3416LV-10-44 | FN3418LV-8-44 | RWK305-7.8-KL | RWK5420-5.9-88-E0XXT | FN5060-12-84 | FN5420-5.9-44-E2FXT | FN3288-10-44-C34-R65 | FN3287-10-44-C28-R65 | FN3288-10-44-C21-R65 | FN3288IT-10-44-C34-R65 | FN3120H-25-33 | FN3280H-8-29-69
6SL32x0-xYC12-xUx0 | SINAMICS G120X Rated power: 1.1 kW | FN3416LV-10-44 | FN3418LV-8-44 | RWK305-7.8-KL | RWK5420-10-88-E0XXT | FN5060-12-84 | FN5420-10-44-E2FXT | FN3416LV-10-44 | FN3418LV-8-44 | RWK305-7.8-KL | RWK5420-10-88-E0XXT | FN5060-12-84 | FN5420-10-44-E2FXT | FN3288-10-44-C34-R65 | FN3287-10-44-C28-R65 | FN3288-10-44-C21-R65 | FN3288IT-10-44-C34-R65 | FN3120H-25-33 | FN3280H-8-29-69
6SL32x0-xYC14-xUx0 | SINAMICS G120X Rated power: 1.5 kW | FN3416LV-10-44 | FN3418LV-11-44 | RWK305-10-KL | RWK5420-10-88-E0XXT | FN5060-12-84 | FN5420-10-44-E2FXT | FN3416LV-10-44 | FN3418LV-11-44 | RWK305-10-KL | RWK5420-10-88-E0XXT | FN5060-12-84 | FN5420-10-44-E2FXT | FN3288-10-44-C34-R65 | FN3287-10-44-C28-R65 | FN3288-10-44-C21-R65 | FN3288IT-10-44-C34-R65 | FN3120H-25-33 | FN3280H-8-29-69
6SL32x0-xYC16-xUx0 | SINAMICS G120X Rated power: 2.2 kW | FN3416LV-16-44 | FN3418LV-15-44 | RWK305-14-KL | RWK5420-13-89-E0XXT | FN5060-12-84 | FN5420-13-33-E2FXT | FN3416LV-16-44 | FN3418LV-15-44 | RWK305-14-KL | RWK5420-13-89-E0XXT | FN5060-12-84 | FN5420-13-33-E2FXT | FN3288-10-44-C34-R65 | FN3287-10-44-C28-R65 | FN3288-10-44-C21-R65 | FN3288IT-10-44-C34-R65 | FN3120H-25-33 | FN3280H-16-29-69
6SL32x0-xYC18-xUx0 | SINAMICS G120X Rated power: 3 kW | FN3416LV-24-33 | FN3418LV-21-33 | RWK305-17-KL | RWK5420-18-89-E0XXT | FN5060-24-84 | FN5420-18-33-E2FXT | FN3416LV-24-33 | FN3418LV-21-33 | RWK305-17-KL | RWK5420-18-89-E0XXT | FN5060-24-84 | FN5420-18-33-E2FXT | FN3288-16-44-C35-R65 | FN3287-16-44-C33-R65 | FN3288-16-44-C21-R65 | FN3288IT-16-44-C34-R65 | FN3120H-25-33 | FN3280H-16-29-69
6SL32x0-xYC20-xUx0 | SINAMICS G120X Rated power: 4 kW | FN3416LV-32-33 | FN3418LV-28-33 | RWK305-24-KL | RWK5420-26-92-E0XXT | FN5060-24-84 | FN5420-26-33-E2FXT | FN3416LV-32-33 | FN3418LV-28-33 | RWK305-24-KL | RWK5420-26-92-E0XXT | FN5060-24-84 | FN5420-26-33-E2FXT | FN3288-16-44-C35-R65 | FN3287-16-44-C33-R65 | FN3288-16-44-C21-R65 | FN3288IT-16-44-C34-R65 | FN3120H-25-33 | FN3280H-25-33-69
6SL32x0-xYC22-xUx0 | SINAMICS G120X Rated power: 5.5 kW | FN3416LV-38-33 | FN3418LV-35-33 | RWK305-24-KL | RWK5420-26-92-E0XXT | FN5060-24-84 | FN5420-26-33-E2FXT | FN3416LV-38-33 | FN3418LV-35-33 | RWK305-32-KL | RWK5420-26-92-E0XXT | FN5060-30-99 | FN5420-26-33-E2FXT | FN3288-25-33-C35-R65 | FN3287-25-33-C33-R65 | FN3288-25-33-C21-R65 | FN3288IT-25-33-C34-R65 | FN3120H-25-33 | FN3280H-25-33-69
6SL32x0-xYC24-xUx0 | SINAMICS G120X Rated power: 7.5 kW | FN3416LV-45-33 | FN3418LV-41-33 | RWK305-32-KL | RWK5420-32-92-E0XXT | FN5060-45-99 | FN5420-32-33-E2FXT | FN3416LV-45-33 | FN3418LV-41-33 | RWK305-45-KL | RWK5420-38-92-E0XXT | FN5060-45-99 | FN5420-38-33-E2FXT | FN3288-40-33-C35-R65 | FN3287-40-33-C33-R65 | FN3288-40-33-C21-R65 | FN3288IT-40-33-C34-R65 | FN3120H-50-53 | FN3280H-36-33-69
6SL32x0-xYC26-xUx0 | SINAMICS G120X Rated power: 11 kW | FN3416LV-60-34 | FN3418LV-65-34 | RWK305-60-KL | RWK5420-60-92-E0XXT | FN5060-60-99 | FN5420-60-34-E2FXT | FN3416LV-60-34 | FN3418LV-53-34 | RWK305-45-KL | RWK5420-45-92-E0XXT | FN5060-45-99 | FN5420-45-34-E2FXT | FN3288-40-33-C35-R65 | FN3287-40-33-C33-R65 | FN3288-40-33-C21-R65 | FN3288IT-40-33-C34-R65 | FN3120H-50-53 | FN3280H-64-34-69
6SL32x0-xYC28-xUx0 | SINAMICS G120X Rated power: 15 kW | FN3416LV-90-35 | FN3418LV-80-35 | RWK305-60-KL | RWK5420-60-92-E0XXT | FN5060-60-99 | FN5420-60-34-E2FXT | FN3416LV-90-35 | FN3418LV-80-35 | RWK305-72-KL | RWK5420-75-99-E0XXT | FN5060-70-99 | FN5420-75-35-E2FXT | FN3288-50-53-C35-R65 | FN3287-50-53-C33-R65 | FN3288-50-53-C21-R65 | FN3288IT-50-53-C34-R65 | FN3120H-80-35 | FN3280H-64-34-69
6SL32x0-xYC30-xUx0 | SINAMICS G120X Rated power: 18.5 kW | FN3416LV-110-35 | FN3418LV-105-35 | RWK305-90-KL | RWK5420-75-99-E0XXT | FN5060-90-99 | FN5420-75-35-E2FXT | FN3416LV-150-40 | FN3418LV-105-35 | RWK305-90-KL | RWK5420-90-99-E0XXT | FN5060-90-99 | FN5420-90-35-E2FXT | FN3288-63-53-C35-R65 | FN3287-63-53-C33-R65 | FN3288-63-53-C21-R65 | FN3288IT-63-53-C34-R65 | FN3120H-80-35 | FN3280H-64-34-69
6SL32x0-xYC32-xUx0 | SINAMICS G120X Rated power: 22 kW | FN3416LV-150-40 | FN3418LV-130-40 | RWK305-90-KL | RWK5420-90-99-E0XXT | FN5060-90-99 | FN5420-90-35-E2FXT | FN3416LV-180-40 | FN3418LV-130-40 | RWK305-110-KL | RWK5420-110-99-E0XXT | FN5060-110-99 | FN5420-110-35-E2FXT | FN3288-80-34-C35-R65 | FN3287-80-34-C33-R65 | FN3288-80-34-C21-R65 | FN3288IT-80-34-C34-R65 | FN3120H-80-35 | FN3280H-80-35-69
6SL32x0-xYC34-xUx0 | SINAMICS G120X Rated power: 30 kW | FN3416LV-180-40 | FN3418LV-160-40 | RWK305-124-KS | RWK5420-145-99-E0XXT | FN5060-150-99 | FN5420-145-99-E0XXT | FN3416LV-180-40 | FN3418LV-160-40 | RWK305-124-KS | RWK5420-145-99-E0XXT | FN5060-150-99 | FN5420-145-99-E0XXT | FN3288-100-35-C35-R65 | FN3287-100-35-C33-R65 | FN3288-100-35-C21-R65 | FN3288IT-100-35-C34-R65 | FN3120H-110-35 | FN3280H-120-35-69
6SL32x0-xYC36-xUx0 | SINAMICS G120X Rated power: 37 kW | FN3416LV-210-40 | FN3418LV-190-40 | RWK305-143-KS | RWK5420-145-99-E0XXT | FN5060-150-99 | FN5420-145-99-E0XXT | FN3416LV-260-99 | FN3418LV-240-99 | RWK305-156-KS | RWK5420-180-99-E0XXT | FN5060-180-99 | FN5420-180-99-E0XXT | FN3288-125-35-C35-R65 | FN3287-125-35-C33-R65 | FN3288-125-35-C21-R65 | FN3288IT-125-35-C34-R65 | FN3120H-150-40 | FN3280H-160-40-69
6SL32x0-xYC38-xUx0 | SINAMICS G120X Rated power: 45 kW | FN3416LV-260-99 | FN3418LV-240-99 | RWK305-170-KS | RWK5420-180-99-E0XXT | FN5060-180-99 | FN5420-180-99-E0XXT | FN3416LV-260-99 | FN3418LV-240-99 | RWK305-230-KS | RWK5420-200-99-E0XXT | FN5060-250-99 | FN5420-200-99-E0XXT | FN3288-160-40-C35-R65 | FN3287-160-40-C33-R65 | FN3288-160-40-C21-R65 | FN3288IT-160-40-C34-R65 | FN3120H-150-40 | FN3280H-160-40-69
6SL32x0-xYC40-xUx0 | SINAMICS G120X Rated power: 55 kW | FN3416LV-320-99 | FN3418LV-310-99 | RWK305-230-KS | RWK5420-250-99-E0XXT | FN5060-250-99 | FN5420-250-99-E0XXT | 2x FN3416LV-210-40 | FN3418LV-310-99 | RWK305-230-KS | RWK5420-250-99-E0XXT | FN5060-250-99 | FN5420-250-99-E0XXT | FN3288-230-40-C35-R65 | FN3287-230-40-C33-R65 | FN3288-230-40-C21-R65 | FN3288IT-230-40-C34-R65 | FN3120H-230-40 | FN3280H-200-40-69

## G120X 380VAC-480VAC
|  | Drive in Low overload (LO) | [12 empty] | Drive in High overload (HO)
G120X 380VAC-480VAC | Power Modul Description | PHF 5% THDi 400V 50Hz LO | PHF 5% THDi 480V 50Hz LO | PHF 5% THDi 380V 60Hz LO | PHF 5% THDi 480V 60Hz LO | PHF 10-15% THDi 400V 50Hz LO | PHF 10-15% THDi 480V 50Hz LO | PHF 10-15% THDi 400V 60Hz LO | PHF 10-15% THDi 480V 60Hz LO | AC Line Reactor LO | dv/dt Reactor 0.8% LO | dv/dt Reactor 6% LO | dv/dt Filter LO | SineWave Filter LO | PHF 5% THDi 400V 50Hz HO | PHF 5% THDi 480V 50Hz HO | PHF 5% THDi 400V 60Hz HO | PHF 5% THDi 480V 60Hz HO | PHF 10-15% THDi 400V 50Hz HO | PHF 10-15% THDi 480V 50Hz HO | PHF 10-15% THDi 400V 60Hz HO | PHF 10-15% THDi 480V 60Hz HO | AC Line Reactor HO | dv/dt Reactor 0.8% HO | dv/dt Reactor 6% HO | dv/dt Filter HO | SineWave Filter HO | EMC Filter Motor Cable Lenght ≤ 50m Class C1 | EMC Filter Motor Cable Lenght ≤ 50m Class C2 | EMC Filter Low Leakage Current Motor Cable Lenght ≤ 35m Class C2 | EMC Filter for IT Power Networks Class C2 | EMC Filter Motor Cable Lenght > 50m Class C1 | EMC Filter 3-Phase with Neutral for Machine Tools and Low Leakage Current Applications
6SL32x0-xYE10-xUx0 | SINAMICS G120X Rated power: 0.75 kW | FN3440-1-110-E2XXJRX | FN3450-1-110-E2XXJRX | FN3442-2-110-E2XXJRX | FN3452-3-110-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-5-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-3.5-88-E0XXX | RWK305-4-KL | RWK5420-3.1-88-E0XXT | FN5060-12-84 | FN5420-3.1-44-E2XXT | FN3440-1-110-E2XXJRX | FN3450-1-110-E2XXJRX | FN3442-1-110-E2XXJRX | FN3452-1-110-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-5-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-2-88-E0XXX | RWK305-4-KL | RWK5420-3.1-88-E0XXT | FN5060-12-84 | FN5420-3.1-44-E2XXT | FN3288-10-44-C34-R65 | FN3287-10-44-C28-R65 | FN3288-10-44-C21-R65 | FN3288IT-10-44-C34-R65 | FN3120H-25-33 | FN3280H-8-29-69
6SL32x0-xYE12-xUx0 | SINAMICS G120X Rated power: 1.1 kW | FN3440-2-110-E2XXJRX | FN3450-1-110-E2XXJRX | FN3442-2-110-E2XXJRX | FN3452-3-110-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-5-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-3.5-88-E0XXX | RWK305-4-KL | RWK5420-5.9-88-E0XXT | FN5060-12-84 | FN5420-5.9-44-E2FXT | FN3440-1-110-E2XXJRX | FN3450-2-110-E2XXJRX | FN3442-1-110-E2XXJRX | FN3452-1-110-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-5-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-3.5-88-E0XXX | RWK305-4-KL | RWK5420-5.9-88-E0XXT | FN5060-12-84 | FN5420-5.9-44-E2FXT | FN3288-10-44-C34-R65 | FN3287-10-44-C28-R65 | FN3288-10-44-C21-R65 | FN3288IT-10-44-C34-R65 | FN3120H-25-33 | FN3280H-8-29-69
6SL32x0-xYE14-xUx0 | SINAMICS G120X Rated power: 1.5 kW | FN3440-2-110-E2XXJRX | FN3450-2-110-E2XXJRX | FN3442-2-110-E2XXJRX | FN3452-3-110-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-5-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-6.5-88-E0XXX | RWK305-7.8-KL | RWK5420-5.9-88-E0XXT | FN5060-12-84 | FN5420-5.9-44-E2FXT | FN3440-1-110-E2XXJRX | FN3450-2-110-E2XXJRX | FN3442-2-110-E2XXJRX | FN3452-3-110-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-5-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-3.5-88-E0XXX | RWK305-7.8-KL | RWK5420-5.9-88-E0XXT | FN5060-12-84 | FN5420-5.9-44-E2FXT | FN3288-10-44-C34-R65 | FN3287-10-44-C28-R65 | FN3288-10-44-C21-R65 | FN3288IT-10-44-C34-R65 | FN3120H-25-33 | FN3280H-8-29-69
6SL32x0-xYE16-xUx0 | SINAMICS G120X Rated power: 2.2 kW | FN3440-2-110-E2XXJRX | FN3450-2-110-E2XXJRX | FN3442-4-112-E2XXJRX | FN3452-5-112-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-5-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-6.5-88-E0XXX | RWK305-7.8-KL | RWK5420-10-88-E0XXT | FN5060-12-84 | FN5420-10-44-E2FXT | FN3440-2-110-E2XXJRX | FN3450-4-112-E2XXJRX | FN3442-2-110-E2XXJRX | FN3452-3-110-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-5-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-6.5-88-E0XXX | RWK305-7.8-KL | RWK5420-10-88-E0XXT | FN5060-12-84 | FN5420-10-44-E2FXT | FN3288-10-44-C34-R65 | FN3287-10-44-C28-R65 | FN3288-10-44-C21-R65 | FN3288IT-10-44-C34-R65 | FN3120H-25-33 | FN3280H-8-29-69
6SL32x0-xYE18-xUx0 | SINAMICS G120X Rated power: 3 kW | FN3440-4-112-E2XXJRX | FN3450-4-112-E2XXJRX | FN3442-4-112-E2XXJRX | FN3452-5-112-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-8-44-E2XXJXX | FN3458-8-44-E2XXJXX | RWK3044-9-88-E0XXX | RWK305-10-KL | RWK5420-10-88-E0XXT | FN5060-12-84 | FN5420-10-44-E2FXT | FN3440-4-112-E2XXJRX | FN3450-4-112-E2XXJRX | FN3442-4-112-E2XXJRX | FN3452-5-112-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-5-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-6.5-88-E0XXX | RWK305-10-KL | RWK5420-10-88-E0XXT | FN5060-12-84 | FN5420-10-44-E2FXT | FN3288-10-44-C34-R65 | FN3287-10-44-C28-R65 | FN3288-10-44-C21-R65 | FN3288IT-10-44-C34-R65 | FN3120H-25-33 | FN3280H-8-29-69
6SL32x0-xYE20-xUx0 | SINAMICS G120X Rated power: 4 kW | FN3440-4-112-E2XXJRX | FN3450-4-112-E2XXJRX | FN3442-6-112-E2XXJRX | FN3452-8-112-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-8-44-E2XXJXX | FN3458-8-44-E2XXJXX | RWK3044-12-88-E0XXX | RWK305-14-KL | RWK5420-13-89-E0XXT | FN5060-12-84 | FN5420-13-33-E2FXT | FN3440-4-112-E2XXJRX | FN3450-6-112-E2XXJRX | FN3442-6-112-E2XXJRX | FN3452-5-112-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-8-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-9-88-E0XXX | RWK305-14-KL | RWK5420-13-89-E0XXT | FN5060-12-84 | FN5420-13-33-E2FXT | FN3288-10-44-C34-R65 | FN3287-10-44-C28-R65 | FN3288-10-44-C21-R65 | FN3288IT-10-44-C34-R65 | FN3120H-25-33 | FN3280H-16-29-69
6SL32x0-xYE22-xUx0 | SINAMICS G120X Rated power: 5.5 kW | FN3440-6-112-E2XXJRX | FN3450-6-112-E2XXJRX | FN3442-8-112-E2XXJRX | FN3452-10-112-E2XXJRX | FN3446-6-44-E2XXJXX | FN3446-6-44-E2XXJXX | FN3458-10-44-E2XXJXX | FN3458-10-44-E2XXJXX | RWK3044-12-88-E0XXX | RWK305-17-KL | RWK5420-18-89-E0XXT | FN5060-24-84 | FN5420-18-33-E2FXT | FN3440-6-112-E2XXJRX | FN3450-6-112-E2XXJRX | FN3442-6-112-E2XXJRX | FN3452-8-112-E2XXJRX | FN3446-6-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-10-44-E2XXJXX | FN3458-8-44-E2XXJXX | RWK3044-12-88-E0XXX | RWK305-17-KL | RWK5420-18-89-E0XXT | FN5060-24-84 | FN5420-18-33-E2FXT | FN3288-16-44-C35-R65 | FN3287-16-44-C33-R65 | FN3288-16-44-C21-R65 | FN3288IT-16-44-C34-R65 | FN3120H-25-33 | FN3280H-16-29-69
6SL32x0-xYE24-xUx0 | SINAMICS G120X Rated power: 7.5 kW | FN3440-8-112-E2XXJRX | FN3450-8-112-E2XXJRX | FN3442-12-112-E2XXJRX | FN3452-15-112-E2XXJRX | FN3446-8-44-E2XXJXX | FN3446-8-44-E2XXJXX | FN3458-15-33-E2FAJXX | FN3458-15-33-E2FAJXX | RWK3044-18-89-E0XXX | RWK305-24-KL | RWK5420-26-92-E0XXT | FN5060-24-84 | FN5420-26-33-E2FXT | FN3440-8-112-E2XXJRX | FN3450-8-112-E2XXJRX | FN3442-12-112-E2XXJRX | FN3452-10-112-E2XXJRX | FN3446-8-44-E2XXJXX | FN3446-6-44-E2XXJXX | FN3458-15-33-E2FAJXX | FN3458-10-44-E2XXJXX | RWK3044-18-89-E0XXX | RWK305-24-KL | RWK5420-26-92-E0XXT | FN5060-24-84 | FN5420-26-33-E2FXT | FN3288-20-33-C35-R65 | FN3287-20-33-C33-R65 | FN3288-20-33-C21-R65 | FN3288IT-20-33-C34-R65 | FN3120H-25-33 | FN3280H-25-33-69
6SL32x0-xYE26-xUx0 | SINAMICS G120X Rated power: 11 kW | FN3440-11-113-E2FAJRX | FN3450-11-112-E2XXJRX | FN3442-16-113-E2FAJRX | FN3452-20-113-E2FAJRX | FN3446-11-33-E2FAJXX | FN3446-11-33-E2FAJXX | FN3458-20-33-E2FAJXX | FN3458-20-33-E2FAJXX | RWK3044-30-92-E0XXX | RWK305-32-KL | RWK5420-32-92-E0XXT | FN5060-30-99 | FN5420-32-33-E2FXT | FN3440-11-113-E2FAJRX | FN3450-15-113-E2FAJRX | FN3442-12-112-E2XXJRX | FN3452-15-112-E2XXJRX | FN3446-11-33-E2FAJXX | FN3446-8-44-E2XXJXX | FN3458-15-33-E2FAJXX | FN3458-15-33-E2FAJXX | RWK3044-24-89-E0XXX | RWK305-32-KL | RWK5420-32-92-E0XXT | FN5060-30-99 | FN5420-32-33-E2FXT | FN3288-25-33-C35-R65 | FN3287-25-33-C33-R65 | FN3288-25-33-C21-R65 | FN3288IT-25-33-C34-R65 | FN3120H-25-33 | FN3280H-25-33-69
6SL32x0-xYE28-xUx0 | SINAMICS G120X Rated power: 15 kW | FN3440-15-113-E2FAJRX | FN3450-15-113-E2FAJRX | FN3442-20-113-E2FAJRX | FN3452-25-113-E2FAJRX | FN3446-15-33-E2FAJXX | FN3446-15-33-E2FAJXX | FN3458-25-33-E2FAJXX | FN3458-25-33-E2FAJXX | RWK3044-30-92-E0XXX | RWK305-45-KL | RWK5420-38-92-E0XXT | FN5060-45-99 | FN5420-38-33-E2FXT | FN3440-15-113-E2FAJRX | FN3450-19-113-E2FAJRX | FN3442-20-113-E2FAJRX | FN3452-20-113-E2FAJRX | FN3446-15-33-E2FAJXX | FN3446-11-33-E2FAJXX | FN3458-25-33-E2FAJXX | FN3458-20-33-E2FAJXX | RWK3044-30-92-E0XXX | RWK305-45-KL | RWK5420-45-92-E0XXT | FN5060-45-99 | FN5420-45-34-E2FXT | FN3288-40-33-C35-R65 | FN3287-40-33-C33-R65 | FN3288-40-33-C21-R65 | FN3288IT-40-33-C34-R65 | FN3120H-50-53 | FN3280H-36-33-69
6SL32x0-xYE30-xUx0 | SINAMICS G120X Rated power: 18.5 kW | FN3440-19-113-E2FAJRX | FN3450-19-113-E2FAJRX | FN3442-24-113-E2FAJRX | FN3452-30-113-E2FAJRX | FN3446-19-33-E2FAJXX | FN3446-19-33-E2FAJXX | FN3458-30-33-E2FAJXX | FN3458-30-33-E2FAJXX | RWK3044-48-92-E0XXX | RWK305-45-KL | RWK5420-45-92-E0XXT | FN5060-45-99 | FN5420-45-34-E2FXT | FN3440-22-115-E2FAJRX | FN3450-22-113-E2FAJRX | FN3442-24-113-E2FAJRX | FN3452-25-113-E2FAJRX | FN3446-19-33-E2FAJXX | FN3446-19-33-E2FAJXX | FN3458-30-33-E2FAJXX | FN3458-25-33-E2FAJXX | RWK3044-48-92-E0XXX | RWK305-60-KL | RWK5420-60-92-E0XXT | FN5060-60-99 | FN5420-60-34-E2FXT | FN3288-40-33-C35-R65 | FN3287-40-33-C33-R65 | FN3288-40-33-C21-R65 | FN3288IT-40-33-C34-R65 | FN3120H-50-53 | FN3280H-36-33-69
6SL32x0-xYE32-xUx0 | SINAMICS G120X Rated power: 22 kW | FN3440-22-115-E2FAJRX | FN3450-22-113-E2FAJRX | FN3442-24-113-E2FAJRX | FN3452-30-113-E2FAJRX | FN3446-19-33-E2FAJXX | FN3446-19-33-E2FAJXX | FN3458-40-34-E2FAJXX | FN3458-40-34-E2FAJXX | RWK3044-48-92-E0XXX | RWK305-60-KL | RWK5420-60-92-E0XXT | FN5060-60-99 | FN5420-60-34-E2FXT | FN3440-30-115-E2FAJRX | FN3450-30-115-E2FAJRX | FN3442-32-115-E2FAJRX | FN3452-30-113-E2FAJRX | FN3446-22-33-E2FAJXX | FN3446-19-33-E2FAJXX | FN3458-40-34-E2FAJXX | FN3458-30-33-E2FAJXX | RWK3044-59-92-E0XXX | RWK305-60-KL | RWK5420-60-92-E0XXT | FN5060-60-99 | FN5420-60-34-E2FXT | FN3288-50-53-C35-R65 | FN3287-50-53-C33-R65 | FN3288-50-53-C21-R65 | FN3288IT-50-53-C34-R65 | FN3120H-50-53 | FN3280H-64-34-69
6SL32x0-xYE34-xUx0 | SINAMICS G120X Rated power: 30 kW | FN3440-30-115-E2FAJRX | FN3450-30-115-E2FAJRX | FN3442-40-115-E2FAJRX | FN3452-50-115-E2FAJRX | FN3446-30-34-E2FAJXX | FN3446-30-34-E2FAJXX | FN3458-50-34-E2FAJXX | FN3458-50-34-E2FAJXX | RWK3044-59-92-E0XXX | RWK305-72-KL | RWK5420-75-99-E0XXT | FN5060-70-99 | FN5420-75-35-E2FXT | FN3440-30-115-E2FAJRX | FN3450-37-115-E2FAJRX | FN3442-40-115-E2FAJRX | FN3452-40-115-E2FAJRX | FN3446-30-34-E2FAJXX | FN3446-22-33-E2FAJXX | FN3458-50-34-E2FAJXX | FN3458-40-34-E2FAJXX | RWK3044-59-92-E0XXX | RWK305-72-KL | RWK5420-75-99-E0XXT | FN5060-70-99 | FN5420-75-35-E2FXT | FN3288-63-53-C35-R65 | FN3287-63-53-C33-R65 | FN3288-63-53-C21-R65 | FN3288IT-63-53-C34-R65 | FN3120H-80-35 | FN3280H-64-34-69
6SL32x0-xYE36-xUx0 | SINAMICS G120X Rated power: 37 kW | FN3440-37-115-E2FAJRX | FN3450-37-115-E2FAJRX | FN3442-48-115-E2FAJRX | FN3452-60-115-E2FAJRX | FN3446-37-34-E2FAJXX | FN3446-37-34-E2FAJXX | FN3458-60-35-E2FAJXX | FN3458-60-35-E2FAJXX | RWK3044-72-99-E0XXX | RWK305-90-KL | RWK5420-90-99-E0XXT | FN5060-90-99 | FN5420-90-35-E2FXT | FN3440-45-115-E2FAJRX | FN3450-45-115-E2FAJRX | FN3442-48-115-E2FAJRX | FN3452-60-115-E2FAJRX | FN3446-37-34-E2FAJXX | FN3446-30-34-E2FAJXX | FN3458-60-35-E2FAJXX | FN3458-50-34-E2FAJXX | RWK3044-88-99-E0XXX | RWK305-90-KL | RWK5420-90-99-E0XXT | FN5060-90-99 | FN5420-90-35-E2FXT | FN3288-80-34-C35-R65 | FN3287-80-34-C33-R65 | FN3288-80-34-C21-R65 | FN3288IT-80-34-C34-R65 | FN3120H-80-35 | FN3280H-80-35-69
6SL32x0-xYE38-xUx0 | SINAMICS G120X Rated power: 45 kW | FN3440-45-115-E2FAJRX | FN3450-45-115-E2FAJRX | FN3442-60-115-E2FAJRX | FN3452-75-115-E2FAJRX | FN3446-45-35-E2FAJXX | FN3446-45-35-E2FAJXX | FN3458-75-35-E2FAJXX | FN3458-75-35-E2FAJXX | RWK3044-88-99-E0XXX | RWK305-110-KL | RWK5420-110-99-E0XXT | FN5060-110-99 | FN5420-110-35-E2FXT | FN3440-55-115-E2FAJRX | FN3450-55-115-E2FAJRX | FN3442-60-115-E2FAJRX | FN3452-60-115-E2FAJRX | FN3446-45-35-E2FAJXX | FN3446-45-35-E2FAJXX | FN3458-75-35-E2FAJXX | FN3458-75-35-E2FAJXX | RWK3044-120-99-E0XXX | RWK305-124-KS | RWK5420-145-99-E0XXT | FN5060-150-99 | FN5420-145-99-E0XXT | FN3288-100-35-C35-R65 | FN3287-100-35-C33-R65 | FN3288-100-35-C21-R65 | FN3288IT-100-35-C34-R65 | FN3120H-110-35 | FN3280H-120-35-69
6SL32x0-xYE40-xUx0 | SINAMICS G120X Rated power: 55 kW | FN3440-55-115-E2FAJRX | FN3450-55-115-E2FAJRX | FN3442-80-115-E2FAJRX | FN3452-100-115-E2FAJRX | FN3446-55-35-E2FAJXX | FN3446-55-35-E2FAJXX | FN3458-100-40-E2FAJXX | FN3458-100-40-E2FAJXX | RWK3044-120-99-E0XXX | RWK305-124-KS | RWK5420-145-99-E0XXT | FN5060-150-99 | FN5420-145-99-E0XXT | FN3440-75-116-E2FAJRX | FN3450-75-115-E2FAJRX | FN3442-80-115-E2FAJRX | FN3452-75-115-E2FAJRX | FN3446-55-35-E2FAJXX | FN3446-55-35-E2FAJXX | FN3458-100-40-E2FAJXX | FN3458-100-40-E2FAJXX | RWK3044-120-99-E0XXX | RWK305-143-KS | RWK5420-145-99-E0XXT | FN5060-150-99 | FN5420-145-99-E0XXT | FN3288-125-35-C35-R65 | FN3287-125-35-C33-R65 | FN3288-125-35-C21-R65 | FN3288IT-125-35-C34-R65 | FN3120H-110-35 | FN3280H-120-35-69
6SL32x0-xYE42-xUx0 | SINAMICS G120X Rated power: 75 kW | FN3440-75-116-E2FAJRX | FN3450-75-115-E2FAJRX | FN3442-100-116-E2FAJRX | FN3452-125-116-E2FAJRX | FN3446-75-40-E2FAJXX | FN3446-75-40-E2FAJXX | FN3458-125-40-E2FAJXX | FN3458-125-40-E2FAJXX | RWK3044-140-99-E0XXX | RWK305-170-KS | RWK5420-180-99-E0XXT | FN5060-180-99 | FN5420-180-99-E0XXT | FN3440-75-116-E2FAJRX | FN3450-90-116-E2FAJRX | FN3442-100-116-E2FAJRX | FN3452-100-115-E2FAJRX | FN3446-75-40-E2FAJXX | FN3446-75-40-E2FAJXX | FN3458-125-40-E2FAJXX | FN3458-100-40-E2FAJXX | RWK3044-180-99-E0XXX | RWK305-170-KS | RWK5420-180-99-E0XXT | FN5060-180-99 | FN5420-180-99-E0XXT | FN3288-160-40-C35-R65 | FN3287-160-40-C33-R65 | FN3288-160-40-C21-R65 | FN3288IT-160-40-C34-R65 | FN3120H-150-40 | FN3280H-160-40-69
6SL32x0-xYE44-xUx0 | SINAMICS G120X Rated power: 90 kW | FN3440-90-116-E2FAJRX | FN3450-90-116-E2FAJRX | FN3442-120-116-E2FAJRX | FN3452-150-116-E2FAJRX | FN3446-90-40-E2FAJXX | FN3446-90-40-E2FAJXX | FN3458-150-40-E2FAJXX | FN3458-150-40-E2FAJXX | RWK3044-180-99-E0XXX | RWK305-230-KS | RWK5420-200-99-E0XXT | FN5060-250-99 | FN5420-200-99-E0XXT | FN3440-110-118-E2FAJRX | FN3450-110-116-E2FAJRX | FN3442-120-116-E2FAJRX | FN3452-150-116-E2FAJRX | FN3446-110-40-E2FAJXX | FN3446-90-40-E2FAJXX | FN3458-200-99-E2FAJXX | FN3458-150-40-E2FAJXX | RWK3044-210-99-E0XXX | RWK305-230-KS | RWK5420-250-99-E0XXT | FN5060-250-99 | FN5420-250-99-E0XXT | FN3288-230-40-C35-R65 | FN3287-230-40-C33-R65 | FN3288-230-40-C21-R65 | FN3288IT-230-40-C34-R65 | FN3120H-230-40 | FN3280H-200-40-69
6SL32x0-xYE46-xUx0 | SINAMICS G120X Rated power: 110 kW | FN3440-110-118-E2FAJRX | FN3450-110-116-E2FAJRX | FN3442-120-116-E2FAJRX | FN3452-150-116-E2FAJRX | FN3446-110-40-E2FAJXX | FN3446-110-40-E2FAJXX | FN3458-200-99-E2FAJXX | FN3458-200-99-E2FAJXX | RWK3044-210-99-E0XXX | RWK305-230-KS | RWK5420-250-99-E0XXT | FN5060-250-99 | FN5420-250-99-E0XXT | FN3440-132-118-E2FAJXX | FN3450-132-118-E2FAJRX | FN3442-160-118-E2FAJRX | FN3452-150-116-E2FAJRX | FN3446-132-99-E2FAJXX | FN3446-110-40-E2FAJXX | FN3458-200-99-E2FAJXX | FN3458-200-99-E2FAJXX | RWK3044-260-99-E0XXX | RWK305-280-KS | RWK5420-300-99-E0XXT | FN5060-320-99 | FN5420-300-99-E0XXT | FN3288-230-40-C35-R65 | FN3287-230-40-C33-R65 | FN3288-230-40-C21-R65 | FN3288IT-230-40-C34-R65 | FN3120H-230-40 | FN3280H-200-40-69
6SL32x0-xYE48-xUx0 | SINAMICS G120X Rated power: 132 kW | FN3440-132-118-E2FAJXX | FN3450-132-118-E2FAJRX | FN3442-200-118-E2FAJXX | FN3452-250-118-E2FAJXX | FN3446-132-99-E2FAJXX | FN3446-132-99-E2FAJXX | FN3458-200-99-E2FAJXX | FN3458-200-99-E2FAJXX | RWK3044-260-99-E0XXX | RWK305-280-KS | RWK5420-300-99-E0XXT | FN5060-320-99 | FN5420-300-99-E0XXT | FN3440-160-118-E2FAJXX | FN3450-160-118-E2FAJXX | FN3442-200-118-E2FAJXX | FN3452-250-118-E2FAJXX | FN3446-160-99-E2FAJXX | FN3446-132-99-E2FAJXX | FN3458-250-99-E2FAJXX | FN3458-200-99-E2FAJXX | RWK3044-320-99-E0XXX | RWK305-330-KS | RWK5420-300-99-E0XXT | FN5060-320-99 | FN5420-300-99-E0XXT | FN3359-250-28 | FN3270H-250-99 | - | FN3359HV-250-28 | FN3359-250-28 | FN3280H-300-99-69
6SL32x0-xYE10-xAx0 | SINAMICS G120X Rated power: 0.75 kW | FN3440-1-110-E2XXJRX | FN3450-1-110-E2XXJRX | FN3442-1-110-E2XXJRX | FN3452-3-110-E2XXJRX | FN3440-1-110-E2XXJRX | FN3446-4-44-E2XXJXX | FN3458-5-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-3.5-88-E0XXX | RWK305-4-KL | RWK5420-3.1-88-E0XXT | FN5060-12-84 | FN5420-3.1-44-E2XXT | FN3440-1-110-E2XXJRX | FN3450-1-110-E2XXJRX | FN3442-1-110-E2XXJRX | FN3452-1-110-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-5-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-2-88-E0XXX | RWK305-4-KL | RWK5420-3.1-88-E0XXT | FN5060-12-84 | FN5420-3.1-44-E2XXT | FN3288-10-44-C34-R65 | FN3287-10-44-C28-R65 | FN3288-10-44-C21-R65 | FN3288IT-10-44-C34-R65 | FN3120H-25-33 | FN3280H-8-29-69
6SL32x0-xYE12-xAx0 | SINAMICS G120X Rated power: 1.1 kW | FN3440-2-110-E2XXJRX | FN3450-1-110-E2XXJRX | FN3442-2-110-E2XXJRX | FN3452-3-110-E2XXJRX | FN3440-2-110-E2XXJRX | FN3446-4-44-E2XXJXX | FN3458-5-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-3.5-88-E0XXX | RWK305-4-KL | RWK5420-5.9-88-E0XXT | FN5060-12-84 | FN5420-5.9-44-E2FXT | FN3440-1-110-E2XXJRX | FN3450-2-110-E2XXJRX | FN3442-1-110-E2XXJRX | FN3452-1-110-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-5-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-3.5-88-E0XXX | RWK305-4-KL | RWK5420-5.9-88-E0XXT | FN5060-12-84 | FN5420-5.9-44-E2FXT | FN3288-10-44-C34-R65 | FN3287-10-44-C28-R65 | FN3288-10-44-C21-R65 | FN3288IT-10-44-C34-R65 | FN3120H-25-33 | FN3280H-8-29-69
6SL32x0-xYE14-xAx0 | SINAMICS G120X Rated power: 1.5 kW | FN3440-2-110-E2XXJRX | FN3450-2-110-E2XXJRX | FN3442-2-110-E2XXJRX | FN3452-3-110-E2XXJRX | FN3440-2-110-E2XXJRX | FN3446-4-44-E2XXJXX | FN3458-5-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-6.5-88-E0XXX | RWK305-7.8-KL | RWK5420-5.9-88-E0XXT | FN5060-12-84 | FN5420-5.9-44-E2FXT | FN3440-1-110-E2XXJRX | FN3450-2-110-E2XXJRX | FN3442-2-110-E2XXJRX | FN3452-3-110-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-5-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-3.5-88-E0XXX | RWK305-7.8-KL | RWK5420-5.9-88-E0XXT | FN5060-12-84 | FN5420-5.9-44-E2FXT | FN3288-10-44-C34-R65 | FN3287-10-44-C28-R65 | FN3288-10-44-C21-R65 | FN3288IT-10-44-C34-R65 | FN3120H-25-33 | FN3280H-8-29-69
6SL32x0-xYE16-xAx0 | SINAMICS G120X Rated power: 2.2 kW | FN3440-2-110-E2XXJRX | FN3450-2-110-E2XXJRX | FN3442-4-112-E2XXJRX | FN3452-5-112-E2XXJRX | FN3440-2-110-E2XXJRX | FN3446-4-44-E2XXJXX | FN3458-5-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-6.5-88-E0XXX | RWK305-7.8-KL | RWK5420-10-88-E0XXT | FN5060-12-84 | FN5420-10-44-E2FXT | FN3440-2-110-E2XXJRX | FN3450-4-112-E2XXJRX | FN3442-2-110-E2XXJRX | FN3452-3-110-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-5-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-6.5-88-E0XXX | RWK305-7.8-KL | RWK5420-10-88-E0XXT | FN5060-12-84 | FN5420-10-44-E2FXT | FN3288-10-44-C34-R65 | FN3287-10-44-C28-R65 | FN3288-10-44-C21-R65 | FN3288IT-10-44-C34-R65 | FN3120H-25-33 | FN3280H-8-29-69
6SL32x0-xYE18-xAx0 | SINAMICS G120X Rated power: 3 kW | FN3440-4-112-E2XXJRX | FN3450-4-112-E2XXJRX | FN3442-4-112-E2XXJRX | FN3452-5-112-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-8-44-E2XXJXX | FN3458-8-44-E2XXJXX | RWK3044-9-88-E0XXX | RWK305-10-KL | RWK5420-10-88-E0XXT | FN5060-12-84 | FN5420-10-44-E2FXT | FN3440-4-112-E2XXJRX | FN3450-4-112-E2XXJRX | FN3442-4-112-E2XXJRX | FN3452-5-112-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-5-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-6.5-88-E0XXX | RWK305-10-KL | RWK5420-10-88-E0XXT | FN5060-12-84 | FN5420-10-44-E2FXT | FN3288-10-44-C34-R65 | FN3287-10-44-C28-R65 | FN3288-10-44-C21-R65 | FN3288IT-10-44-C34-R65 | FN3120H-25-33 | FN3280H-8-29-69
6SL32x0-xYE20-xAx0 | SINAMICS G120X Rated power: 4 kW | FN3440-4-112-E2XXJRX | FN3450-4-112-E2XXJRX | FN3442-6-112-E2XXJRX | FN3452-8-112-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-8-44-E2XXJXX | FN3458-8-44-E2XXJXX | RWK3044-12-88-E0XXX | RWK305-14-KL | RWK5420-13-89-E0XXT | FN5060-12-84 | FN5420-13-33-E2FXT | FN3440-4-112-E2XXJRX | FN3450-6-112-E2XXJRX | FN3442-6-112-E2XXJRX | FN3452-5-112-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-8-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-9-88-E0XXX | RWK305-14-KL | RWK5420-13-89-E0XXT | FN5060-12-84 | FN5420-13-33-E2FXT | FN3288-10-44-C34-R65 | FN3287-10-44-C28-R65 | FN3288-10-44-C21-R65 | FN3288IT-10-44-C34-R65 | FN3120H-25-33 | FN3280H-16-29-69
6SL32x0-xYE22-xAx0 | SINAMICS G120X Rated power: 5.5 kW | FN3440-6-112-E2XXJRX | FN3450-6-112-E2XXJRX | FN3442-8-112-E2XXJRX | FN3452-10-112-E2XXJRX | FN3446-6-44-E2XXJXX | FN3446-6-44-E2XXJXX | FN3458-10-44-E2XXJXX | FN3458-10-44-E2XXJXX | RWK3044-12-88-E0XXX | RWK305-17-KL | RWK5420-18-89-E0XXT | FN5060-24-84 | FN5420-18-33-E2FXT | FN3440-6-112-E2XXJRX | FN3450-6-112-E2XXJRX | FN3442-6-112-E2XXJRX | FN3452-8-112-E2XXJRX | FN3446-6-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-10-44-E2XXJXX | FN3458-8-44-E2XXJXX | RWK3044-12-88-E0XXX | RWK305-17-KL | RWK5420-18-89-E0XXT | FN5060-24-84 | FN5420-18-33-E2FXT | FN3288-16-44-C35-R65 | FN3287-16-44-C33-R65 | FN3288-16-44-C21-R65 | FN3288IT-16-44-C34-R65 | FN3120H-25-33 | FN3280H-16-29-69
6SL32x0-xYE24-xAx0 | SINAMICS G120X Rated power: 7.5 kW | FN3440-8-112-E2XXJRX | FN3450-8-112-E2XXJRX | FN3442-12-112-E2XXJRX | FN3452-15-112-E2XXJRX | FN3446-8-44-E2XXJXX | FN3446-8-44-E2XXJXX | FN3458-15-33-E2FAJXX | FN3458-15-33-E2FAJXX | RWK3044-18-89-E0XXX | RWK305-24-KL | RWK5420-26-92-E0XXT | FN5060-24-84 | FN5420-26-33-E2FXT | FN3440-8-112-E2XXJRX | FN3450-8-112-E2XXJRX | FN3442-12-112-E2XXJRX | FN3452-10-112-E2XXJRX | FN3446-8-44-E2XXJXX | FN3446-6-44-E2XXJXX | FN3458-15-33-E2FAJXX | FN3458-10-44-E2XXJXX | RWK3044-18-89-E0XXX | RWK305-24-KL | RWK5420-26-92-E0XXT | FN5060-24-84 | FN5420-26-33-E2FXT | FN3288-20-33-C35-R65 | FN3287-20-33-C33-R65 | FN3288-20-33-C21-R65 | FN3288IT-20-33-C34-R65 | FN3120H-25-33 | FN3280H-25-33-69
6SL32x0-xYE26-xAx0 | SINAMICS G120X Rated power: 11 kW | FN3440-11-113-E2FAJRX | FN3450-11-112-E2XXJRX | FN3442-16-113-E2FAJRX | FN3452-20-113-E2FAJRX | FN3446-11-33-E2FAJXX | FN3446-11-33-E2FAJXX | FN3458-20-33-E2FAJXX | FN3458-20-33-E2FAJXX | RWK3044-30-92-E0XXX | RWK305-32-KL | RWK5420-32-92-E0XXT | FN5060-30-99 | FN5420-32-33-E2FXT | FN3440-11-113-E2FAJRX | FN3450-15-113-E2FAJRX | FN3442-12-112-E2XXJRX | FN3452-15-112-E2XXJRX | FN3446-11-33-E2FAJXX | FN3446-8-44-E2XXJXX | FN3458-15-33-E2FAJXX | FN3458-15-33-E2FAJXX | RWK3044-24-89-E0XXX | RWK305-32-KL | RWK5420-32-92-E0XXT | FN5060-30-99 | FN5420-32-33-E2FXT | FN3288-25-33-C35-R65 | FN3287-25-33-C33-R65 | FN3288-25-33-C21-R65 | FN3288IT-25-33-C34-R65 | FN3120H-25-33 | FN3280H-25-33-69
6SL32x0-xYE28-xAx0 | SINAMICS G120X Rated power: 15 kW | FN3440-15-113-E2FAJRX | FN3450-15-113-E2FAJRX | FN3442-20-113-E2FAJRX | FN3452-25-113-E2FAJRX | FN3446-15-33-E2FAJXX | FN3446-15-33-E2FAJXX | FN3458-25-33-E2FAJXX | FN3458-25-33-E2FAJXX | RWK3044-30-92-E0XXX | RWK305-45-KL | RWK5420-38-92-E0XXT | FN5060-45-99 | FN5420-38-33-E2FXT | FN3440-15-113-E2FAJRX | FN3450-19-113-E2FAJRX | FN3442-20-113-E2FAJRX | FN3452-20-113-E2FAJRX | FN3446-15-33-E2FAJXX | FN3446-11-33-E2FAJXX | FN3458-25-33-E2FAJXX | FN3458-20-33-E2FAJXX | RWK3044-30-92-E0XXX | RWK305-45-KL | RWK5420-45-92-E0XXT | FN5060-45-99 | FN5420-45-34-E2FXT | FN3288-40-33-C35-R65 | FN3287-40-33-C33-R65 | FN3288-40-33-C21-R65 | FN3288IT-40-33-C34-R65 | FN3120H-50-53 | FN3280H-36-33-69
6SL32x0-xYE30-xAx0 | SINAMICS G120X Rated power: 18.5 kW | FN3440-19-113-E2FAJRX | FN3450-19-113-E2FAJRX | FN3442-24-113-E2FAJRX | FN3452-30-113-E2FAJRX | FN3446-19-33-E2FAJXX | FN3446-19-33-E2FAJXX | FN3458-30-33-E2FAJXX | FN3458-30-33-E2FAJXX | RWK3044-48-92-E0XXX | RWK305-45-KL | RWK5420-45-92-E0XXT | FN5060-45-99 | FN5420-45-34-E2FXT | FN3440-22-115-E2FAJRX | FN3450-22-113-E2FAJRX | FN3442-24-113-E2FAJRX | FN3452-25-113-E2FAJRX | FN3446-19-33-E2FAJXX | FN3446-19-33-E2FAJXX | FN3458-30-33-E2FAJXX | FN3458-25-33-E2FAJXX | RWK3044-48-92-E0XXX | RWK305-60-KL | RWK5420-60-92-E0XXT | FN5060-60-99 | FN5420-60-34-E2FXT | FN3288-40-33-C35-R65 | FN3287-40-33-C33-R65 | FN3288-40-33-C21-R65 | FN3288IT-40-33-C34-R65 | FN3120H-50-53 | FN3280H-36-33-69
6SL32x0-xYE32-xAx0 | SINAMICS G120X Rated power: 22 kW | FN3440-22-115-E2FAJRX | FN3450-22-113-E2FAJRX | FN3442-32-115-E2FAJRX | FN3452-30-113-E2FAJRX | FN3446-22-33-E2FAJXX | FN3446-19-33-E2FAJXX | FN3458-40-34-E2FAJXX | FN3458-40-34-E2FAJXX | RWK3044-48-92-E0XXX | RWK305-60-KL | RWK5420-60-92-E0XXT | FN5060-60-99 | FN5420-60-34-E2FXT | FN3440-30-115-E2FAJRX | FN3450-30-115-E2FAJRX | FN3442-32-115-E2FAJRX | FN3452-30-113-E2FAJRX | FN3446-22-33-E2FAJXX | FN3446-19-33-E2FAJXX | FN3458-40-34-E2FAJXX | FN3458-30-33-E2FAJXX | RWK3044-59-92-E0XXX | RWK305-60-KL | RWK5420-60-92-E0XXT | FN5060-60-99 | FN5420-60-34-E2FXT | FN3288-50-53-C35-R65 | FN3287-50-53-C33-R65 | FN3288-50-53-C21-R65 | FN3288IT-50-53-C34-R65 | FN3120H-50-53 | FN3280H-64-34-69
6SL32x0-xYE34-xAx0 | SINAMICS G120X Rated power: 30 kW | FN3440-30-115-E2FAJRX | FN3450-30-115-E2FAJRX | FN3442-40-115-E2FAJRX | FN3452-50-115-E2FAJRX | FN3446-30-34-E2FAJXX | FN3446-30-34-E2FAJXX | FN3458-50-34-E2FAJXX | FN3458-50-34-E2FAJXX | RWK3044-59-92-E0XXX | RWK305-72-KL | RWK5420-75-99-E0XXT | FN5060-70-99 | FN5420-75-35-E2FXT | FN3440-30-115-E2FAJRX | FN3450-37-115-E2FAJRX | FN3442-40-115-E2FAJRX | FN3452-40-115-E2FAJRX | FN3446-30-34-E2FAJXX | FN3446-22-33-E2FAJXX | FN3458-50-34-E2FAJXX | FN3458-40-34-E2FAJXX | RWK3044-59-92-E0XXX | RWK305-72-KL | RWK5420-75-99-E0XXT | FN5060-70-99 | FN5420-75-35-E2FXT | FN3288-63-53-C35-R65 | FN3287-63-53-C33-R65 | FN3288-63-53-C21-R65 | FN3288IT-63-53-C34-R65 | FN3120H-80-35 | FN3280H-64-34-69
6SL32x0-xYE36-xAx0 | SINAMICS G120X Rated power: 37 kW | FN3440-37-115-E2FAJRX | FN3450-37-115-E2FAJRX | FN3442-48-115-E2FAJRX | FN3452-60-115-E2FAJRX | FN3446-37-34-E2FAJXX | FN3446-37-34-E2FAJXX | FN3458-60-35-E2FAJXX | FN3458-60-35-E2FAJXX | RWK3044-72-99-E0XXX | RWK305-90-KL | RWK5420-90-99-E0XXT | FN5060-90-99 | FN5420-90-35-E2FXT | FN3440-45-115-E2FAJRX | FN3450-45-115-E2FAJRX | FN3442-48-115-E2FAJRX | FN3452-60-115-E2FAJRX | FN3446-37-34-E2FAJXX | FN3446-30-34-E2FAJXX | FN3458-60-35-E2FAJXX | FN3458-50-34-E2FAJXX | RWK3044-88-99-E0XXX | RWK305-90-KL | RWK5420-90-99-E0XXT | FN5060-90-99 | FN5420-90-35-E2FXT | FN3288-80-34-C35-R65 | FN3287-80-34-C33-R65 | FN3288-80-34-C21-R65 | FN3288IT-80-34-C34-R65 | FN3120H-80-35 | FN3280H-80-35-69
6SL32x0-xYE38-xAx0 | SINAMICS G120X Rated power: 45 kW | FN3440-45-115-E2FAJRX | FN3450-45-115-E2FAJRX | FN3442-60-115-E2FAJRX | FN3452-75-115-E2FAJRX | FN3446-45-35-E2FAJXX | FN3446-45-35-E2FAJXX | FN3458-75-35-E2FAJXX | FN3458-75-35-E2FAJXX | RWK3044-88-99-E0XXX | RWK305-110-KL | RWK5420-110-99-E0XXT | FN5060-110-99 | FN5420-110-35-E2FXT | FN3440-55-115-E2FAJRX | FN3450-55-115-E2FAJRX | FN3442-60-115-E2FAJRX | FN3452-60-115-E2FAJRX | FN3446-45-35-E2FAJXX | FN3446-45-35-E2FAJXX | FN3458-75-35-E2FAJXX | FN3458-75-35-E2FAJXX | RWK3044-120-99-E0XXX | RWK305-124-KS | RWK5420-145-99-E0XXT | FN5060-150-99 | FN5420-145-99-E0XXT | FN3288-100-35-C35-R65 | FN3287-100-35-C33-R65 | FN3288-100-35-C21-R65 | FN3288IT-100-35-C34-R65 | FN3120H-110-35 | FN3280H-120-35-69
6SL32x0-xYE40-xAx0 | SINAMICS G120X Rated power: 55 kW | FN3440-55-115-E2FAJRX | FN3450-55-115-E2FAJRX | FN3442-80-115-E2FAJRX | FN3452-100-115-E2FAJRX | FN3446-55-35-E2FAJXX | FN3446-55-35-E2FAJXX | FN3458-100-40-E2FAJXX | FN3458-100-40-E2FAJXX | RWK3044-120-99-E0XXX | RWK305-124-KS | RWK5420-145-99-E0XXT | FN5060-150-99 | FN5420-145-99-E0XXT | FN3440-75-116-E2FAJRX | FN3450-75-115-E2FAJRX | FN3442-80-115-E2FAJRX | FN3452-75-115-E2FAJRX | FN3446-55-35-E2FAJXX | FN3446-55-35-E2FAJXX | FN3458-100-40-E2FAJXX | FN3458-100-40-E2FAJXX | RWK3044-120-99-E0XXX | RWK305-143-KS | RWK5420-145-99-E0XXT | FN5060-150-99 | FN5420-145-99-E0XXT | FN3288-125-35-C35-R65 | FN3287-125-35-C33-R65 | FN3288-125-35-C21-R65 | FN3288IT-125-35-C34-R65 | FN3120H-110-35 | FN3280H-120-35-69
6SL32x0-xYE42-xAx0 | SINAMICS G120X Rated power: 75 kW | FN3440-75-116-E2FAJRX | FN3450-75-115-E2FAJRX | FN3442-100-116-E2FAJRX | FN3452-125-116-E2FAJRX | FN3446-75-40-E2FAJXX | FN3446-75-40-E2FAJXX | FN3458-125-40-E2FAJXX | FN3458-125-40-E2FAJXX | RWK3044-140-99-E0XXX | RWK305-170-KS | RWK5420-180-99-E0XXT | FN5060-180-99 | FN5420-180-99-E0XXT | FN3440-75-116-E2FAJRX | FN3450-90-116-E2FAJRX | FN3442-100-116-E2FAJRX | FN3452-100-115-E2FAJRX | FN3446-75-40-E2FAJXX | FN3446-75-40-E2FAJXX | FN3458-125-40-E2FAJXX | FN3458-100-40-E2FAJXX | RWK3044-180-99-E0XXX | RWK305-170-KS | RWK5420-180-99-E0XXT | FN5060-180-99 | FN5420-180-99-E0XXT | FN3288-160-40-C35-R65 | FN3287-160-40-C33-R65 | FN3288-160-40-C21-R65 | FN3288IT-160-40-C34-R65 | FN3120H-150-40 | FN3280H-160-40-69
6SL32x0-xYE44-xAx0 | SINAMICS G120X Rated power: 90 kW | FN3440-90-116-E2FAJRX | FN3450-90-116-E2FAJRX | FN3442-120-116-E2FAJRX | FN3452-150-116-E2FAJRX | FN3446-90-40-E2FAJXX | FN3446-90-40-E2FAJXX | FN3458-150-40-E2FAJXX | FN3458-150-40-E2FAJXX | RWK3044-180-99-E0XXX | RWK305-230-KS | RWK5420-200-99-E0XXT | FN5060-250-99 | FN5420-200-99-E0XXT | FN3440-110-118-E2FAJRX | FN3450-110-116-E2FAJRX | FN3442-120-116-E2FAJRX | FN3452-150-116-E2FAJRX | FN3446-110-40-E2FAJXX | FN3446-90-40-E2FAJXX | FN3458-200-99-E2FAJXX | FN3458-150-40-E2FAJXX | RWK3044-210-99-E0XXX | RWK305-230-KS | RWK5420-250-99-E0XXT | FN5060-250-99 | FN5420-250-99-E0XXT | FN3288-230-40-C35-R65 | FN3287-230-40-C33-R65 | FN3288-230-40-C21-R65 | FN3288IT-230-40-C34-R65 | FN3120H-230-40 | FN3280H-200-40-69
6SL32x0-xYE46-xAx0 | SINAMICS G120X Rated power: 110 kW | FN3440-110-118-E2FAJRX | FN3450-110-116-E2FAJRX | FN3442-120-116-E2FAJRX | FN3452-150-116-E2FAJRX | FN3446-110-40-E2FAJXX | FN3446-110-40-E2FAJXX | FN3458-200-99-E2FAJXX | FN3458-200-99-E2FAJXX | RWK3044-210-99-E0XXX | RWK305-230-KS | RWK5420-250-99-E0XXT | FN5060-250-99 | FN5420-250-99-E0XXT | FN3440-132-118-E2FAJXX | FN3450-132-118-E2FAJRX | FN3442-160-118-E2FAJRX | FN3452-150-116-E2FAJRX | FN3446-132-99-E2FAJXX | FN3446-110-40-E2FAJXX | FN3458-200-99-E2FAJXX | FN3458-200-99-E2FAJXX | RWK3044-260-99-E0XXX | RWK305-280-KS | RWK5420-300-99-E0XXT | FN5060-320-99 | FN5420-300-99-E0XXT | FN3288-230-40-C35-R65 | FN3287-230-40-C33-R65 | FN3288-230-40-C21-R65 | FN3288IT-230-40-C34-R65 | FN3120H-230-40 | FN3280H-200-40-69
6SL32x0-xYE48-xAx0 | SINAMICS G120X Rated power: 132 kW | FN3440-132-118-E2FAJXX | FN3450-132-118-E2FAJRX | FN3442-200-118-E2FAJXX | FN3452-250-118-E2FAJXX | FN3446-132-99-E2FAJXX | FN3446-132-99-E2FAJXX | FN3458-200-99-E2FAJXX | FN3458-200-99-E2FAJXX | RWK3044-260-99-E0XXX | RWK305-280-KS | RWK5420-300-99-E0XXT | FN5060-320-99 | FN5420-300-99-E0XXT | FN3440-160-118-E2FAJXX | FN3450-160-118-E2FAJXX | FN3442-200-118-E2FAJXX | FN3452-250-118-E2FAJXX | FN3446-160-99-E2FAJXX | FN3446-132-99-E2FAJXX | FN3458-250-99-E2FAJXX | FN3458-200-99-E2FAJXX | RWK3044-320-99-E0XXX | RWK305-330-KS | RWK5420-300-99-E0XXT | FN5060-320-99 | FN5420-300-99-E0XXT | FN3359-250-28 | FN3270H-250-99 | - | FN3359HV-250-28 | FN3359-250-28 | FN3280H-300-99-69
6SL32x0-xYE50-xxx0 | SINAMICS G120X Rated power: 160 kW | FN3440-160-118-E2FAJXX | FN3450-160-118-E2FAJXX | FN3442-200-118-E2FAJXX | FN3452-250-118-E2FAJXX | FN3446-200-99-E2FAJXX | FN3446-160-99-E2FAJXX | FN3458-250-99-E2FAJXX | FN3458-250-99-E2FAJXX | RWK3044-320-99-E0XXX | RWK305-330-KS | RWK5420-400-99-E0XXT | FN5060-400-99 | FN5420-400-99-E0XXT | FN3440-200-118-E2FAJXX | FN3450-200-118-E2FAJXX | FN3442-240-118-E2FAJXX | FN3452-250-118-E2FAJXX | FN3446-200-99-E2FAJXX | FN3446-160-99-E2FAJXX | FN3458-300-99-E2FAJXX | FN3458-250-99-E2FAJXX | RWK3044-400-99-E0XXX | RWK305-400-S | RWK5420-400-99-E0XXT | FN5060-400-99 | FN5420-400-99-E0XXT | FN3359-320-99 | FN3270H-320-99 | - | FN3359HV-320-99 | FN3359-320-99 | FN3280H-400-99-69
6SL32x0-xYE52-xxx0 | SINAMICS G120X Rated power: 200 kW | FN3440-200-118-E2FAJXX | FN3450-200-118-E2FAJXX | FN3442-240-118-E2FAJXX | FN3452-300-118-E2FAJXX | FN3446-200-99-E2FAJXX | FN3446-200-99-E2FAJXX | FN3458-300-99-E2FAJXX | FN3458-300-99-E2FAJXX | RWK3044-400-99-E0XXX | RWK305-400-S | RWK5420-400-99-E0XXT | FN5060-400-99 | FN5420-400-99-E0XXT | FN3440-250-119-E2FASXX | FN3450-250-118-E2FAJXX | FN3472-280-99-E0XXJXX | FN3452-300-118-E2FAJXX | FN3471-250-99-E0XXJXX | FN3446-200-99-E2FAJXX | FN3473-280-99-E0XXJXX | FN3458-300-99-E2FAJXX | RWK3044-510-99-E0XXX | RWK305-500-S | RWK5420-480-99-E0XXT | FN5060-500-99 | FN5420-480-99-E0XXT | FN3359-400-99 | FN3270H-400-99 | - | FN3359HV-400-99 | FN3359-400-99 | FN3280H-600-99-69
6SL32x0-xYE54-xxx0 | SINAMICS G120X Rated power: 250 kW | FN3440-250-119-E2FASXX | FN3450-250-118-E2FAJXX | FN3472-280-99-E0XXJXX | FN3482-350-99-E0XXJXX | FN3471-250-99 | FN3481-315-99-E0XXJXX | FN3473-280-99-E0XXJXX | FN3483-350-99-E0XXJXX | RWK3044-510-99-E0XXX | RWK305-600-S | RWK5420-630-99-E0XXT | FN5060-600-99 | FN5420-630-99-E0XXT | FN3470-315-99-E0XXJXX | FN3480-315-99-E0XXJXX | FN3472-315-99-E0XXJXX | FN3482-350-99-E0XXJXX | FN3471-315-99-E0XXJXX | FN3481-315-99-E0XXJXX | FN3473-315-99-E0XXJXX | FN3483-350-99-E0XXJXX | RWK3044-570-99-E0XXX | RWK305-600-S | RWK5420-630-99-E0XXT | FN5060-600-99 | FN5420-630-99-E0XXT | FN3359-600-99 | FN3270H-600-99 | - | FN3359HV-600-99 | FN3359-600-99 | FN3280H-600-99-69
6SL32x0-xYE56-xCx0 | SINAMICS G120X Rated power: 315 kW | FN3471-315-99-E0XXJXX | FN3480-315-99-E0XXJXX | FN3472-355-99-E0XXJXX | FN3482-450-99-E0XXJXX | FN3471-315-99 | FN3481-355-99-E0XXJXX | FN3473-355-99-E0XXJXX | FN3483-450-99-E0XXJXX | RWK3044-640-99-E0XXX | RWK305-680-S | RWK5420-630-99-E0XXT | FN5060-700-99 | FN5420-630-99-E0XXT | FN3470-355-99-E0XXJXX | FN3480-315-99-E0XXJXX | FN3472-480-99-E0XXJXX | FN3482-450-99-E0XXJXX | FN3471-355-99-E0XXJXX | FN3481-315-99-E0XXJXX | FN3473-480-99-E0XXJXX | FN3483-450-99-E0XXJXX | RWK3044-800-99-E0XXX | RWK305-790-S | RWK5420-710-99-E0XXT | FN5060-700-99 | FN5420-710-99-E0XXT | FN3359-600-99 | FN3270H-600-99 | - | FN3359HV-600-99 | FN3359-600-99 | FN3280H-600-99-69
6SL32x0-xYE58-xCx0 | SINAMICS G120X Rated power: 355 kW | FN3470-355-99-E0XXJXX | FN3480-355-99-E0XXJXX | FN3472-400-99-E0XXJXX | FN3482-500-99-E0XXJXX | FN3471-355-99 | FN3481-400-99-E0XXJXX | FN3473-400-99-E0XXJXX | FN3483-500-99-E0XXJXX | RWK3044-800-99-E0XXX | RWK305-790-S | RWK5420-710-99-E0XXT | FN5060-700-99 | FN5420-710-99-E0XXT | FN3470-500-99-E0XXJXX | FN3480-400-99-E0XXJXX | 2x FN3472-315-99-E0XXJXX | FN3482-600-99-E0XXJXX | FN3471-500-99-E0XXJXX | FN3481-400-99-E0XXJXX | 2x FN3473-315-99-E0XXJXX | FN3483-600-99-E0XXJXX | RWK3044-1000-99-E0XXX | RWK305-790-S | RWK5420-800-99-E0XXT | FN5060-900-99 | FN5420-800-99-E0XXT | FN3359-800-99 | FN3270H-800-99 | - | FN3359HV-800-99 | FN3359-800-99 | -
6SL32x0-xYE60-xCx0 | SINAMICS G120X Rated power: 400 kW | FN3470-400-99-E0XXJXX | FN3480-400-99-E0XXJXX | FN3472-480-99-E0XXJXX | FN3482-600-99-E0XXJXX | FN3471-400-99 | FN3481-500-99-E0XXJXX | FN3473-480-99-E0XXJXX | FN3483-600-99-E0XXJXX | RWK3044-800-99-E0XXX | RWK305-790-S | RWK5420-800-99-E0XXT | FN5060-900-99 | FN5420-800-99-E0XXT | FN3470-500-99-E0XXJXX | FN3480-500-99-E0XXJXX | 2x FN3472-315-99-E0XXJXX | 2x FN3482-400-99-E0XXJXX | FN3471-500-99-E0XXJXX | FN3481-500-99-E0XXJXX | 2x FN3473-315-99-E0XXJXX | 2x FN3483-400-99-E0XXJXX | RWK3044-1000-99-E0XXX | RWK305-910-S | RWK5420-1000-99-E0XXT | FN5060-900-99 | FN5420-1000-99-E0XXT | FN3359-800-99 | FN3270H-800-99 | - | FN3359HV-800-99 | FN3359-800-99 | -
6SL32x0-xYE62-xCx0 | SINAMICS G120X Rated power: 450 kW | FN3470-500-99-E0XXJXX | FN3480-500-99-E0XXJXX | 2x FN3472-315-99-E0XXJXX | 2x FN3482-400-99-E0XXJXX | FN3471-500-99 | FN3481-500-99-E0XXJXX | 2x FN3473-315-99-E0XXJXX | 2x FN3483-400-99-E0XXJXX | RWK3044-1000-99-E0XXX | RWK305-910-S | RWK5420-1000-99-E0XXT | FN5060-900-99 | FN5420-1000-99-E0XXT | 2x FN3470-315-99-E0XXJXX | FN3480-560-99-E0XXJXX | 2x FN3472-315-99-E0XXJXX | 2x FN3482-400-99-E0XXJXX | 2x FN3471-315-99-E0XXJXX | FN3481-560-99-E0XXJXX | 2x FN3473-315-99-E0XXJXX | 2x FN3483-400-99-E0XXJXX | 2x RWK3044-640-99-E0XXX | RWK305-1100-S | RWK5420-1000-99-E0XXT | FN5060-1100-99 | FN5420-1000-99-E0XXT | FN3359-1000-99 | FN3270H-1000-99 | - | FN3359HV-1000-99 | FN3359-1000-99 | -
6SL32x0-xYE64-xCx0 | SINAMICS G120X Rated power: 500 kW | FN3470-500-99-E0XXJXX | FN3480-500-99-E0XXJXX | 2x FN3472-315-99-E0XXJXX | 2x FN3482-400-99-E0XXJXX | FN3471-500-99 | FN3481-560-99-E0XXJXX | 2x FN3473-315-99-E0XXJXX | 2x FN3483-400-99-E0XXJXX | RWK3044-1000-99-E0XXX | RWK305-1100-S | RWK5420-1000-99-E0XXT | FN5060-1100-99 | FN5420-1000-99-E0XXT | 2x FN3470-315-99-E0XXJXX | 2x FN3480-315-99-E0XXJXX | 2x FN3472-400-99-E0XXJXX | 2x FN3482-400-99-E0XXJXX | 2x FN3471-315-99-E0XXJXX | 2x FN3481-355-99-E0XXJXX | 2x FN3473-400-99-E0XXJXX | 2x FN3483-400-99-E0XXJXX | 2x RWK3044-640-99-E0XXX | RWK305-1100-S | 2x RWK5420-630-99-E0XXT | FN5060-1100-99 | 2x FN5420-630-99-E0XXT | FN3359-1000-99 | FN3270H-1000-99 | - | FN3359HV-1000-99 | FN3359-1000-99 | -
6SL32x0-xYE66-xCx0 | SINAMICS G120X Rated power: 560 kW | 2x FN3470-315-99-E0XXJXX | FN3480-560-99-E0XXJXX | 2x FN3472-315-99-E0XXJXX | 2x FN3482-400-99-E0XXJXX | 2x FN3471-315-99 | 2x FN3481-355-99-E0XXJXX | 2x FN3473-315-99-E0XXJXX | 2x FN3483-400-99-E0XXJXX | 2x RWK3044-640-99-E0XXX | RWK305-1100-S | 2x RWK5420-630-99-E0XXT | FN5060-1100-99 | 2x FN5420-630-99-E0XXT | 2x FN3470-355-99-E0XXJXX | 2x FN3480-315-99-E0XXJXX | 2x FN3472-480-99-E0XXJXX | 2x FN3482-450-99-E0XXJXX | 2x FN3471-355-99-E0XXJXX | 2x FN3481-355-99-E0XXJXX | 2x FN3473-480-99-E0XXJXX | 2x FN3483-450-99-E0XXJXX | 2x RWK3044-800-99-E0XXX | 2x RWK305-600-S | 2x RWK5420-630-99-E0XXT | 2x FN5060-600-99 | 2x FN5420-630-99-E0XXT | FN3359-1600-99 | FN3359-1600-99 | - | FN3359HV-1600-99 | FN3359-1600-99 | -

## G120X 500VAC-690VAC
|  | Drive in Low overload (LO) |  |  | Drive in High overload (HO)
G120X 500VAC-690VAC | Power Modul Description | AC Line Reactor LO | dv/dt Filter LO | SineWave Filter LO | AC Line Reactor HO | dv/dt Filter HO | SineWave Filter HO | EMC Filter Motor Cable Lenght ≤ 50m Class C1 | EMC Filter Motor Cable Lenght ≤ 50m Class C2 | EMC Filter for IT Power Networks Class C2
6SL32x0-xYH18-xUx0 | SINAMICS G120X Rated power: 3 kW | RWK3062-5.5-88-E0XXX | FN5060HV-30-99 | FN5040HV-13-83 | RWK3062-7.5-88-E0XXX | FN5060HV-30-99 | FN5040HV-13-83 | FN3288HV-10-44-C34-R65 | FN3288HV-10-44-C34-R65 | FN3288HVIT-10-44-C42-R65
6SL32x0-xYH20-xUx0 | SINAMICS G120X Rated power: 4 kW | RWK3062-7.5-88-E0XXX | FN5060HV-30-99 | FN5040HV-13-83 | RWK3062-10-88-E0XXX | FN5060HV-30-99 | FN5040HV-13-83 | FN3288HV-10-44-C34-R65 | FN3288HV-10-44-C34-R65 | FN3288HVIT-10-44-C42-R65
6SL32x0-xYH22-xUx0 | SINAMICS G120X Rated power: 5.5 kW | RWK3062-10-88-E0XXX | FN5060HV-30-99 | FN5040HV-13-83 | RWK3062-15-89-E0XXX | FN5060HV-30-99 | FN5040HV-13-83 | FN3288HV-10-44-C34-R65 | FN3288HV-10-44-C34-R65 | FN3288HVIT-10-44-C42-R65
6SL32x0-xYH24-xUx0 | SINAMICS G120X Rated power: 7.5 kW | RWK3062-15-89-E0XXX | FN5060HV-30-99 | FN5040HV-13-83 | RWK3062-15-89-E0XXX | FN5060HV-30-99 | FN5040HV-28-84 | FN3288HV-16-44-C34-R65 | FN3288HV-16-44-C34-R65 | FN3288HVIT-16-44-C43-R65
6SL32x0-xYH26-xUx0 | SINAMICS G120X Rated power: 11 kW | RWK3062-15-89-E0XXX | FN5060HV-30-99 | FN5040HV-28-84 | RWK3062-21-89-E0XXX | FN5060HV-30-99 | FN5040HV-28-84 | FN3288HV-16-44-C34-R65 | FN3288HV-16-44-C34-R65 | FN3288HVIT-16-44-C43-R65
6SL32x0-xYH28-xUx0 | SINAMICS G120X Rated power: 15 kW | RWK3062-21-89-E0XXX | FN5060HV-30-99 | FN5040HV-28-84 | RWK3062-30-92-E0XXX | FN5060HV-30-99 | FN5040HV-28-84 | FN3288HV-20-33-C36-R65 | FN3288HV-20-33-C36-R65 | FN3288HVIT-20-33-C43-R65
6SL32x0-xYH30-xUx0 | SINAMICS G120X Rated power: 18.5 kW | RWK3062-26-92-E0XXX | FN5060HV-30-99 | FN5040HV-28-84 | RWK3062-41-92-E0XXX | FN5060HV-30-99 | FN5040HV-28-84 | FN3288HV-25-33-C36-R65 | FN3288HV-25-33-C36-R65 | FN3288HVIT-25-33-C43-R65
6SL32x0-xYH32-xUx0 | SINAMICS G120X Rated power: 22 kW | RWK3062-26-92-E0XXX | FN5060HV-30-99 | FN5040HV-45-86 | RWK3062-51-92-E0XXX | FN5060HV-45-99 | FN5040HV-45-86 | FN3288HV-25-33-C36-R65 | FN3288HV-25-33-C36-R65 | FN3288HVIT-25-33-C43-R65
6SL32x0-xYH34-xUx0 | SINAMICS G120X Rated power: 30 kW | RWK3062-41-92-E0XXX | FN5060HV-45-99 | FN5040HV-45-86 | RWK3062-62-99-E0XXX | FN5060HV-45-99 | FN5040HV-45-86 | FN3288HV-40-33-C36-R65 | FN3288HV-40-33-C36-R65 | FN3288HVIT-40-33-C43-R65
6SL32x0-xYH36-xUx0 | SINAMICS G120X Rated power: 37 kW | RWK3062-41-92-E0XXX | FN5060HV-75-99 | FN5040HV-75-99 | RWK3062-100-99-E0XXX | FN5060HV-75-99 | FN5040HV-75-99 | FN3288HV-40-33-C36-R65 | FN3288HV-40-33-C36-R65 | FN3288HVIT-40-33-C43-R65
6SL32x0-xYH38-xUx0 | SINAMICS G120X Rated power: 45 kW | RWK3062-51-92-E0XXX | FN5060HV-75-99 | FN5040HV-75-99 | RWK3062-100-99-E0XXX | FN5060HV-75-99 | FN5040HV-75-99 | FN3288HV-50-53-C36-R65 | FN3288HV-50-53-C36-R65 | FN3288HVIT-50-53-C43-R65
6SL32x0-xYH40-xUx0 | SINAMICS G120X Rated power: 55 kW | RWK3062-62-99-E0XXX | FN5060HV-75-99 | FN5040HV-75-99 | RWK3062-120-99-E0XXX | FN5060HV-115-99 | FN5040HV-115-99 | FN3288HV-63-53-C36-R65 | FN3288HV-63-53-C36-R65 | FN3288HVIT-63-53-C43-R65
6SL32x0-xYH42-xUx0 | SINAMICS G120X Rated power: 75 kW | RWK3062-100-99-E0XXX | FN5060HV-115-99 | FN5040HV-115-99 | RWK3062-150-99-E0XXX | FN5060HV-115-99 | FN5040HV-115-99 | FN3288HV-80-34-C36-R65 | FN3288HV-80-34-C36-R65 | FN3288HVIT-80-34-C43-R65
6SL32x0-xYH44-xUx0 | SINAMICS G120X Rated power: 90 kW | RWK3062-100-99-E0XXX | FN5060HV-115-99 | FN5040HV-115-99 | RWK3062-220-99-E0XXX | FN5060HV-165-99 | FN5040HV-165-99 | FN3288HV-100-35-C36-R65 | FN3288HV-100-35-C36-R65 | FN3288HVIT-100-35-C43-R65
6SL32x0-xYH46-xUx0 | SINAMICS G120X Rated power: 110 kW | RWK3062-120-99-E0XXX | FN5060HV-165-99 | FN5040HV-165-99 | RWK3062-280-99-E0XXX | FN5060HV-165-99 | FN5040HV-165-99 | FN3288HV-125-35-C36-R65 | FN3288HV-125-35-C36-R65 | FN3288HVIT-125-35-C44-R65
6SL32x0-xYH48-xUx0 | SINAMICS G120X Rated power: 132 kW | RWK3062-150-99-E0XXX | FN5060HV-165-99 | FN5040HV-165-99 | RWK3062-350-99-E0XXX | FN5060HV-220-99 | FN5040HV-260-99 | FN3288HV-160-40-C36-R65 | FN3288HV-160-40-C36-R65 | FN3288HVIT-160-40-C43-R65
6SL32x0-xYH18-xAx0 | SINAMICS G120X Rated power: 3 kW | RWK3062-5.5-88-E0XXX | FN5060HV-30-99 | FN5040HV-13-83 | RWK3062-7.5-88-E0XXX | FN5060HV-30-99 | FN5040HV-13-83 | FN3288HV-10-44-C34-R65 | FN3288HV-10-44-C34-R65 | FN3288HVIT-10-44-C42-R65
6SL32x0-xYH20-xAx0 | SINAMICS G120X Rated power: 4 kW | RWK3062-7.5-88-E0XXX | FN5060HV-30-99 | FN5040HV-13-83 | RWK3062-10-88-E0XXX | FN5060HV-30-99 | FN5040HV-13-83 | FN3288HV-10-44-C34-R65 | FN3288HV-10-44-C34-R65 | FN3288HVIT-10-44-C42-R65
6SL32x0-xYH22-xAx0 | SINAMICS G120X Rated power: 5.5 kW | RWK3062-10-88-E0XXX | FN5060HV-30-99 | FN5040HV-13-83 | RWK3062-15-89-E0XXX | FN5060HV-30-99 | FN5040HV-13-83 | FN3288HV-10-44-C34-R65 | FN3288HV-10-44-C34-R65 | FN3288HVIT-10-44-C42-R65
6SL32x0-xYH24-xAx0 | SINAMICS G120X Rated power: 7.5 kW | RWK3062-15-89-E0XXX | FN5060HV-30-99 | FN5040HV-13-83 | RWK3062-15-89-E0XXX | FN5060HV-30-99 | FN5040HV-28-84 | FN3288HV-16-44-C34-R65 | FN3288HV-16-44-C34-R65 | FN3288HVIT-16-44-C43-R65
6SL32x0-xYH26-xAx0 | SINAMICS G120X Rated power: 11 kW | RWK3062-15-89-E0XXX | FN5060HV-30-99 | FN5040HV-28-84 | RWK3062-21-89-E0XXX | FN5060HV-30-99 | FN5040HV-28-84 | FN3288HV-16-44-C34-R65 | FN3288HV-16-44-C34-R65 | FN3288HVIT-16-44-C43-R65
6SL32x0-xYH28-xAx0 | SINAMICS G120X Rated power: 15 kW | RWK3062-21-89-E0XXX | FN5060HV-30-99 | FN5040HV-28-84 | RWK3062-30-92-E0XXX | FN5060HV-30-99 | FN5040HV-28-84 | FN3288HV-20-33-C36-R65 | FN3288HV-20-33-C36-R65 | FN3288HVIT-20-33-C43-R65
6SL32x0-xYH30-xAx0 | SINAMICS G120X Rated power: 18.5 kW | RWK3062-26-92-E0XXX | FN5060HV-30-99 | FN5040HV-28-84 | RWK3062-41-92-E0XXX | FN5060HV-30-99 | FN5040HV-28-84 | FN3288HV-25-33-C36-R65 | FN3288HV-25-33-C36-R65 | FN3288HVIT-25-33-C43-R65
6SL32x0-xYH32-xAx0 | SINAMICS G120X Rated power: 22 kW | RWK3062-26-92-E0XXX | FN5060HV-30-99 | FN5040HV-45-86 | RWK3062-51-92-E0XXX | FN5060HV-45-99 | FN5040HV-45-86 | FN3288HV-25-33-C36-R65 | FN3288HV-25-33-C36-R65 | FN3288HVIT-25-33-C43-R65
6SL32x0-xYH34-xAx0 | SINAMICS G120X Rated power: 30 kW | RWK3062-41-92-E0XXX | FN5060HV-45-99 | FN5040HV-45-86 | RWK3062-62-99-E0XXX | FN5060HV-45-99 | FN5040HV-45-86 | FN3288HV-40-33-C36-R65 | FN3288HV-40-33-C36-R65 | FN3288HVIT-40-33-C43-R65
6SL32x0-xYH36-xAx0 | SINAMICS G120X Rated power: 37 kW | RWK3062-41-92-E0XXX | FN5060HV-75-99 | FN5040HV-75-99 | RWK3062-100-99-E0XXX | FN5060HV-75-99 | FN5040HV-75-99 | FN3288HV-40-33-C36-R65 | FN3288HV-40-33-C36-R65 | FN3288HVIT-40-33-C43-R65
6SL32x0-xYH38-xAx0 | SINAMICS G120X Rated power: 45 kW | RWK3062-51-92-E0XXX | FN5060HV-75-99 | FN5040HV-75-99 | RWK3062-100-99-E0XXX | FN5060HV-75-99 | FN5040HV-75-99 | FN3288HV-50-53-C36-R65 | FN3288HV-50-53-C36-R65 | FN3288HVIT-50-53-C43-R65
6SL32x0-xYH40-xAx0 | SINAMICS G120X Rated power: 55 kW | RWK3062-62-99-E0XXX | FN5060HV-75-99 | FN5040HV-75-99 | RWK3062-120-99-E0XXX | FN5060HV-115-99 | FN5040HV-115-99 | FN3288HV-63-53-C36-R65 | FN3288HV-63-53-C36-R65 | FN3288HVIT-63-53-C43-R65
6SL32x0-xYH42-xCx0 | SINAMICS G120X Rated power: 75 kW | RWK3062-100-99-E0XXX | FN5060HV-115-99 | FN5040HV-115-99 | RWK3062-150-99-E0XXX | FN5060HV-115-99 | FN5040HV-115-99 | FN3288HV-80-34-C36-R65 | FN3288HV-80-34-C36-R65 | FN3288HVIT-80-34-C43-R65
6SL32x0-xYH44-xCx0 | SINAMICS G120X Rated power: 90 kW | RWK3062-100-99-E0XXX | FN5060HV-115-99 | FN5040HV-115-99 | RWK3062-220-99-E0XXX | FN5060HV-165-99 | FN5040HV-165-99 | FN3288HV-100-35-C36-R65 | FN3288HV-100-35-C36-R65 | FN3288HVIT-100-35-C43-R65
6SL32x0-xYH46-xCx0 | SINAMICS G120X Rated power: 110 kW | RWK3062-120-99-E0XXX | FN5060HV-165-99 | FN5040HV-165-99 | RWK3062-280-99-E0XXX | FN5060HV-165-99 | FN5040HV-165-99 | FN3288HV-125-35-C36-R65 | FN3288HV-125-35-C36-R65 | FN3288HVIT-125-35-C44-R65
6SL32x0-xYH48-xCx0 | SINAMICS G120X Rated power: 132 kW | RWK3062-150-99-E0XXX | FN5060HV-165-99 | FN5040HV-165-99 | RWK3062-350-99-E0XXX | FN5060HV-220-99 | FN5040HV-260-99 | FN3288HV-160-40-C36-R65 | FN3288HV-160-40-C36-R65 | FN3288HVIT-160-40-C43-R65
6SL32x0-xYH50-xCx0 | SINAMICS G120X Rated power: 160 kW | RWK3062-180-99-E0XXX | FN5060HV-220-99 | FN5040HV-260-99 | RWK3062-440-99-E0XXX | FN5060HV-220-99 | FN5040HV-260-99 | FN3288HV-230-40-C36-R65 | FN3288HV-230-40-C36-R65 | FN3288HVIT-230-40-C34-R65
6SL32x0-xYH52-xCx0 | SINAMICS G120X Rated power: 200 kW | RWK3062-220-99-E0XXX | FN5060HV-320-99 | FN5040HV-260-99 | RWK3062-440-99-E0XXX | FN5060HV-320-99 | FN5040HV-260-99 | FN3288HV-230-40-C36-R65 | FN3288HV-230-40-C36-R65 | FN3288HVIT-230-40-C34-R65
6SL32x0-xYH54-xCx0 | SINAMICS G120X Rated power: 250 kW | RWK3062-280-99-E0XXX | FN5060HV-320-99 | FN5040HV-300-99 | RWK3062-550-99-E0XXX | FN5060HV-320-99 | FN5040HV-430-99 | FN3359HV-250-28 | FN3359HV-250-28 | FN3311HVIT-250-99-C18-R5
6SL32x0-xYH56-xCx0 | SINAMICS G120X Rated power: 315 kW | RWK3062-350-99-E0XXX | FN5060HV-450-99 | FN5040HV-430-99 | RWK3062-690-99-E0XXX | FN5060HV-450-99 | FN5040HV-430-99 | FN3359HV-400-99 | FN3359HV-400-99 | FN3311HVIT-400-99-C18-R5
6SL32x0-xYH58-xCx0 | SINAMICS G120X Rated power: 355 kW | RWK3062-440-99-E0XXX | FN5060HV-450-99 | FN5040HV-430-99 | RWK3062-870-99-E0XXX | FN5060HV-660-99 | FN5040HV-530-99 | FN3359HV-400-99 | FN3359HV-400-99 | FN3311HVIT-400-99-C18-R5
6SL32x0-xYH60-xCx0 | SINAMICS G120X Rated power: 400 kW | RWK3062-490-99-E0XXX | FN5060HV-660-99 | FN5040HV-530-99 | 2x RWK3062-490-99-E0XXX | FN5060HV-660-99 | FN5040HV-530-99 | FN3359HV-600-99 | FN3359HV-600-99 | FN3311HVIT-600-99-C18-R5
6SL32x0-xYH62-xCx0 | SINAMICS G120X Rated power: 450 kW | RWK3062-490-99-E0XXX | FN5060HV-660-99 | FN5040HV-530-99 | 2x RWK3062-550-99-E0XXX | FN5060HV-660-99 | FN5040HV-660-99 | FN3359HV-600-99 | FN3359HV-600-99 | FN3311HVIT-600-99-C18-R5
6SL32x0-xYH64-xCx0 | SINAMICS G120X Rated power: 500 kW | RWK3062-550-99-E0XXX | FN5060HV-660-99 | FN5040HV-660-99 | 2x RWK3062-690-99-E0XXX | FN5060HV-660-99 | FN5040HV-660-99 | FN3359HV-600-99 | FN3359HV-600-99 | FN3311HVIT-600-99-C18-R5
6SL32x0-xYH66-xCx0 | SINAMICS G120X Rated power: 560 kW | RWK3062-690-99-E0XXX | FN5060HV-660-99 | FN5040HV-660-99 | 2x RWK3062-690-99-E0XXX | FN5060HV-900-99 | FN5040HV-765-99 | FN3359HV-600-99 | FN3359HV-600-99 | FN3311HVIT-600-99-C18-R5
6SL32x0-xYH68-xCx0 | SINAMICS G120X Rated power: 630 kW | RWK3062-690-99-E0XXX | FN5060HV-900-99 | FN5040HV-765-99 | 2x RWK3062-870-99-E0XXX | FN5060HV-900-99 | FN5040HV-940-99 | FN3359HV-1000-99 | FN3359HV-1000-99 | FN3311HVIT-1000-99-C18-R5

## G220 200VAC-240VAC
|  | Drive in Low overload (LO) | [5 empty] | Drive in High overload (HO)
G220 200VAC-240VAC | Power Modul Description | PHF 200-240V 50Hz LO | PHF 200-240V 60Hz LO | dv/dt Reactor 0.8% LO | dv/dt Reactor 6% LO | dv/dt Filter LO | SineWave Filter LO | PHF 200V 50Hz HO | PHF 240V 60Hz HO | dv/dt Reactor 0.8% HO | dv/dt Reactor 6% HO | dv/dt Filter HO | SineWave Filter HO | EMC Filter Motor Cable Lenght ≤ 50m Class C1 | EMC Filter Motor Cable Lenght ≤ 50m Class C2 | EMC Filter Low Leakage Current Motor Cable Lenght ≤ 35m Class C2 | EMC Filter for IT Power Networks Class C2 | EMC Filter Motor Cable Lenght > 50m Class C1 | EMC Filter 3-Phase with Neutral for Machine Tools and Low Leakage Current Applications
6SL4112-0xA05-0xx0 | SINAMICS G220, 3AC 200...240V, 0.55kW | FN3416LV-10-44 | FN3418LV-8-44 | RWK305-7.8-KL | RWK5420-5.9-88-E0XXT | FN5060-12-84 | FN5420-5.9-44-E2FXT | FN3416LV-10-44 | FN3418LV-8-44 | RWK305-7.8-KL | RWK5420-5.9-88-E0XXT | FN5060-12-84 | FN5420-5.9-44-E2FXT | FN3288-10-44-C34-R65 | FN3287-10-44-C28-R65 | FN3288-10-44-C21-R65 | FN3288IT-10-44-C34-R65 | FN3120H-25-33 | FN3280H-8-29-69
6SL4112-0xA06-0xx0 | SINAMICS G220, 3AC 200...240V, 0,75kW | FN3416LV-10-44 | FN3418LV-8-44 | RWK305-7.8-KL | RWK5420-5.9-88-E0XXT | FN5060-12-84 | FN5420-5.9-44-E2FXT | FN3416LV-10-44 | FN3418LV-8-44 | RWK305-7.8-KL | RWK5420-5.9-88-E0XXT | FN5060-12-84 | FN5420-5.9-44-E2FXT | FN3288-10-44-C34-R65 | FN3287-10-44-C28-R65 | FN3288-10-44-C21-R65 | FN3288IT-10-44-C34-R65 | FN3120H-25-33 | FN3280H-8-29-69
6SL4112-0xA08-0xx0 | SINAMICS G220, 3AC 200...240V, 1.1kW | FN3416LV-10-44 | FN3418LV-8-44 | RWK305-7.8-KL | RWK5420-10-88-E0XXT | FN5060-12-84 | FN5420-10-44-E2FXT | FN3416LV-10-44 | FN3418LV-8-44 | RWK305-7.8-KL | RWK5420-10-88-E0XXT | FN5060-12-84 | FN5420-10-44-E2FXT | FN3288-10-44-C34-R65 | FN3287-10-44-C28-R65 | FN3288-10-44-C21-R65 | FN3288IT-10-44-C34-R65 | FN3120H-25-33 | FN3280H-8-29-69
6SL4112-0xA10-0xx0 | SINAMICS G220, 3AC 200...240V, 1.5kW | FN3416LV-10-44 | FN3418LV-11-44 | RWK305-10-KL | RWK5420-10-88-E0XXT | FN5060-12-84 | FN5420-10-44-E2FXT | FN3416LV-10-44 | FN3418LV-11-44 | RWK305-10-KL | RWK5420-10-88-E0XXT | FN5060-12-84 | FN5420-10-44-E2FXT | FN3288-10-44-C34-R65 | FN3287-10-44-C28-R65 | FN3288-10-44-C21-R65 | FN3288IT-10-44-C34-R65 | FN3120H-25-33 | FN3280H-8-29-69
6SL4112-0xA11-0xx0 | SINAMICS G220, 3AC 200...240V, 2,2kW | FN3416LV-16-44 | FN3418LV-15-44 | RWK305-14-KL | RWK5420-13-89-E0XXT | FN5060-12-84 | FN5420-13-33-E2FXT | FN3416LV-16-44 | FN3418LV-15-44 | RWK305-14-KL | RWK5420-13-89-E0XXT | FN5060-24-84 | FN5420-13-33-E2FXT | FN3288-10-44-C34-R65 | FN3287-10-44-C28-R65 | FN3288-10-44-C21-R65 | FN3288IT-10-44-C34-R65 | FN3120H-25-33 | FN3280H-16-29-69
6SL4112-0xA12-0xx0 | SINAMICS G220, 3AC 200...240V, 3kW | FN3416LV-24-33 | FN3418LV-21-33 | RWK305-17-KL | RWK5420-18-89-E0XXT | FN5060-24-84 | FN5420-18-33-E2FXT | FN3416LV-24-33 | FN3418LV-21-33 | RWK305-17-KL | RWK5420-18-89-E0XXT | FN5060-24-84 | FN5420-18-33-E2FXT | FN3288-16-44-C35-R65 | FN3287-16-44-C33-R65 | FN3288-16-44-C21-R65 | FN3288IT-16-44-C34-R65 | FN3120H-25-33 | FN3280H-16-29-69
6SL4112-0xA13-0xx0 | SINAMICS G220, 3AC 200...240V, 4kW | FN3416LV-32-33 | FN3418LV-28-33 | RWK305-24-KL | RWK5420-26-92-E0XXT | FN5060-24-84 | FN5420-26-33-E2FXT | FN3416LV-32-33 | FN3418LV-28-33 | RWK305-24-KL | RWK5420-26-92-E0XXT | FN5060-24-84 | FN5420-26-33-E2FXT | FN3288-20-33-C35-R65 | FN3287-20-33-C33-R65 | FN3288-20-33-C21-R65 | FN3288IT-20-33-C34-R65 | FN3120H-25-33 | FN3280H-25-33-69
6SL4112-0xA15-0xx0 | SINAMICS G220, 3AC 200...240V, 5.5kW | FN3416LV-38-33 | FN3418LV-35-33 | RWK305-32-KL | RWK5420-32-92-E0XXT | FN5060-30-99 | FN5420-32-33-E2FXT | FN3416LV-38-33 | FN3418LV-35-33 | RWK305-32-KL | RWK5420-32-92-E0XXT | FN5060-30-99 | FN5420-32-33-E2FXT | FN3288-25-33-C35-R65 | FN3287-25-33-C33-R65 | FN3288-25-33-C21-R65 | FN3288IT-25-33-C34-R65 | FN3120H-25-33 | FN3280H-25-33-69
6SL4112-0xA16-0xx0 | SINAMICS G220, 3AC 200...240V, 7.5kW | FN3416LV-45-33 | FN3418LV-41-33 | RWK305-45-KL | RWK5420-38-92-E0XXT | FN5060-45-99 | FN5420-38-33-E2FXT | FN3416LV-45-33 | FN3418LV-41-33 | RWK305-45-KL | RWK5420-45-92-E0XXT | FN5060-45-99 | FN5420-45-34-E2FXT | FN3288-40-33-C35-R65 | FN3287-40-33-C33-R65 | FN3288-40-33-C21-R65 | FN3288IT-40-33-C34-R65 | FN3120H-50-53 | FN3280H-36-33-69
6SL4112-0xA17-0xx0 | SINAMICS G220, 3AC 200...240V, 11kW | FN3416LV-60-34 | FN3418LV-65-34 | RWK305-60-KL | RWK5420-60-92-E0XXT | FN5060-60-99 | FN5420-60-34-E2FXT | FN3416LV-60-34 | FN3418LV-53-34 | RWK305-60-KL | RWK5420-60-92-E0XXT | FN5060-60-99 | FN5420-60-34-E2FXT | FN3288-50-53-C35-R65 | FN3287-50-53-C33-R65 | FN3288-50-53-C21-R65 | FN3288IT-50-53-C34-R65 | FN3120H-50-53 | FN3280H-64-34-69
6SL4112-0xA18-0xx0 | SINAMICS G220, 3AC 200...240V, 15kW | FN3416LV-90-35 | FN3418LV-80-35 | RWK305-72-KL | RWK5420-75-99-E0XXT | FN5060-70-99 | FN5420-75-35-E2FXT | FN3416LV-90-35 | FN3418LV-80-35 | RWK305-72-KL | RWK5420-75-99-E0XXT | FN5060-70-99 | FN5420-75-35-E2FXT | FN3288-63-53-C35-R65 | FN3287-63-53-C33-R65 | FN3288-63-53-C21-R65 | FN3288IT-63-53-C34-R65 | FN3120H-80-35 | FN3280H-64-34-69
6SL4112-0xA20-0xx0 | SINAMICS G220, 3AC 200...240V, 18.5kW | FN3416LV-110-35 | FN3418LV-105-35 | RWK305-90-KL | RWK5420-90-99-E0XXT | FN5060-90-99 | FN5420-90-35-E2FXT | FN3416LV-150-40 | FN3418LV-105-35 | RWK305-110-KL | RWK5420-110-99-E0XXT | FN5060-110-99 | FN5420-110-35-E2FXT | FN3288-80-34-C35-R65 | FN3287-80-34-C33-R65 | FN3288-80-34-C21-R65 | FN3288IT-80-34-C34-R65 | FN3120H-80-35 | FN3280H-80-35-69
6SL4112-0xA21-0xx0 | SINAMICS G220, 3AC 200...240V, 22kW | FN3416LV-150-40 | FN3418LV-130-40 | RWK305-110-KL | RWK5420-110-99-E0XXT | FN5060-110-99 | FN5420-110-35-E2FXT | FN3416LV-180-40 | FN3418LV-130-40 | RWK305-124-KS | RWK5420-145-99-E0XXT | FN5060-150-99 | FN5420-145-99-E0XXT | FN3288-80-34-C35-R65 | FN3287-80-34-C33-R65 | FN3288-80-34-C21-R65 | FN3288IT-80-34-C34-R65 | FN3120H-80-35 | FN3280H-80-35-69
6SL4112-0xA23-0xx0 | SINAMICS G220, 3AC 200...240V, 30kW | FN3416LV-180-40 | FN3418LV-160-40 | RWK305-124-KS | RWK5420-145-99-E0XXT | FN5060-150-99 | FN5420-145-99-E0XXT | FN3416LV-180-40 | FN3418LV-160-40 | RWK305-143-KS | RWK5420-145-99-E0XXT | FN5060-150-99 | FN5420-145-99-E0XXT | FN3288-125-35-C35-R65 | FN3287-125-35-C33-R65 | FN3288-125-35-C21-R65 | FN3288IT-125-35-C34-R65 | FN3120H-110-35 | FN3280H-120-35-69

## G220 380VAC-500VAC
|  | Drive in Low overload (LO) | [12 empty] | Drive in High overload (HO)
G220 380VAC-500VAC | Power Modul Description | PHF 5% THDi 400V 50Hz LO | PHF 5% THDi 480V 50Hz LO | PHF 5% THDi 380V 60Hz LO | PHF 5% THDi 480V 60Hz LO | PHF 10-15% THDi 400V 50Hz LO | PHF 10-15% THDi 480V 50Hz LO | PHF 10-15% THDi 400V 60Hz LO | PHF 10-15% THDi 480V 60Hz LO | AC Line Reactor LO | dv/dt Reactor 0.8% LO | dv/dt Reactor 6% LO | dv/dt Filter LO | SineWave Filter LO | PHF 5% THDi 400V 50Hz HO | PHF 5% THDi 480V 50Hz HO | PHF 5% THDi 400V 60Hz HO | PHF 5% THDi 480V 60Hz HO | PHF 10-15% THDi 400V 50Hz HO | PHF 10-15% THDi 480V 50Hz HO | PHF 10-15% THDi 400V 60Hz HO | PHF 10-15% THDi 480V 60Hz HO | AC Line Reactor HO | dv/dt Reactor 0.8% HO | dv/dt Reactor 6% HO | dv/dt Filter HO | SineWave Filter HO | EMC Filter Motor Cable Lenght ≤ 50m Class C1 | EMC Filter Motor Cable Lenght ≤ 50m Class C2 | EMC Filter Low Leakage Current Motor Cable Lenght ≤ 35m Class C2 | EMC Filter for IT Power Networks Class C2 | EMC Filter Motor Cable Lenght > 50m Class C1 | EMC Filter 3-Phase with Neutral for Machine Tools and Low Leakage Current Applications
6SL4113-0xA08-0xx0 | SINAMICS G220, 3AC 380...415/440...500V, 1.1kW | FN3440-2-110-E2XXJRX | FN3450-4-112-E2XXJRX | FN3442-2-110-E2XXJRX | FN3452-3-110-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-5-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-3.5-88-E0XXX | RWK305-7.8-KL | RWK5420-5.9-88-E0XXT | FN5060-12-84 | FN5420-5.9-44-E2FXT | FN3440-1-110-E2XXJRX | FN3450-2-110-E2XXJRX | FN3442-2-110-E2XXJRX | FN3452-3-110-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-5-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-3.5-88-E0XXX | RWK305-7.8-KL | RWK5420-5.9-88-E0XXT | FN5060-12-84 | FN5420-5.9-44-E2FXT | FN3288-10-44-C34-R65 | FN3287-10-44-C28-R65 | FN3288-10-44-C21-R65 | FN3288IT-10-44-C34-R65 | FN3120H-25-33 | FN3280H-8-29-69
6SL4113-0xA10-0xx0 | SINAMICS G220, 3AC 380...415/440...500V, 1.5kW | FN3440-2-110-E2XXJRX | FN3450-4-112-E2XXJRX | FN3442-4-112-E2XXJRX | FN3452-5-112-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-5-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-6.5-88-E0XXX | RWK305-7.8-KL | RWK5420-5.9-88-E0XXT | FN5060-12-84 | FN5420-5.9-44-E2FXT | FN3440-1-110-E2XXJRX | FN3450-2-110-E2XXJRX | FN3442-4-112-E2XXJRX | FN3452-5-112-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-5-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-3.5-88-E0XXX | RWK305-7.8-KL | RWK5420-5.9-88-E0XXT | FN5060-12-84 | FN5420-5.9-44-E2FXT | FN3288-10-44-C34-R65 | FN3287-10-44-C28-R65 | FN3288-10-44-C21-R65 | FN3288IT-10-44-C34-R65 | FN3120H-25-33 | FN3280H-8-29-69
6SL4113-0xA11-0xx0 | SINAMICS G220, 3AC 380...415/440...500V, 2,2kW | FN3440-4-112-E2XXJRX | FN3450-6-112-E2XXJRX | FN3442-4-112-E2XXJRX | FN3452-5-112-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-5-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-6.5-88-E0XXX | RWK305-7.8-KL | RWK5420-10-88-E0XXT | FN5060-12-84 | FN5420-10-44-E2FXT | FN3440-2-110-E2XXJRX | FN3450-4-112-E2XXJRX | FN3442-4-112-E2XXJRX | FN3452-5-112-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-5-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-6.5-88-E0XXX | RWK305-7.8-KL | RWK5420-10-88-E0XXT | FN5060-12-84 | FN5420-10-44-E2FXT | FN3288-10-44-C34-R65 | FN3287-10-44-C28-R65 | FN3288-10-44-C21-R65 | FN3288IT-10-44-C34-R65 | FN3120H-25-33 | FN3280H-8-29-69
6SL4113-0xA12-0xx0 | SINAMICS G220, 3AC 380...415/440...500V, 3kW | FN3440-4-112-E2XXJRX | FN3450-6-112-E2XXJRX | FN3442-6-112-E2XXJRX | FN3452-8-112-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-8-44-E2XXJXX | FN3458-8-44-E2XXJXX | RWK3044-9-88-E0XXX | RWK305-10-KL | RWK5420-10-88-E0XXT | FN5060-12-84 | FN5420-10-44-E2FXT | FN3440-4-112-E2XXJRX | FN3450-4-112-E2XXJRX | FN3442-6-112-E2XXJRX | FN3452-8-112-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-5-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-6.5-88-E0XXX | RWK305-10-KL | RWK5420-10-88-E0XXT | FN5060-12-84 | FN5420-10-44-E2FXT | FN3288-10-44-C34-R65 | FN3287-10-44-C28-R65 | FN3288-10-44-C21-R65 | FN3288IT-10-44-C34-R65 | FN3120H-25-33 | FN3280H-8-29-69
6SL4113-0xA13-0xx0 | SINAMICS G220, 3AC 380...415/440...500V, 4kW | FN3440-4-112-E2XXJRX | FN3450-6-112-E2XXJRX | FN3442-6-112-E2XXJRX | FN3452-8-112-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-8-44-E2XXJXX | FN3458-8-44-E2XXJXX | RWK3044-12-88-E0XXX | RWK305-14-KL | RWK5420-13-89-E0XXT | FN5060-12-84 | FN5420-13-33-E2FXT | FN3440-4-112-E2XXJRX | FN3450-6-112-E2XXJRX | FN3442-8-112-E2XXJRX | FN3452-10-112-E2XXJRX | FN3446-6-44-E2XXJXX | FN3446-6-44-E2XXJXX | FN3458-8-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-9-88-E0XXX | RWK305-14-KL | RWK5420-13-89-E0XXT | FN5060-24-84 | FN5420-13-33-E2FXT | FN3288-10-44-C34-R65 | FN3287-10-44-C28-R65 | FN3288-10-44-C21-R65 | FN3288IT-10-44-C34-R65 | FN3120H-25-33 | FN3280H-16-29-69
6SL4113-0xA15-0xx0 | SINAMICS G220, 3AC 380...415/440...500V, 5.5kW | FN3440-6-112-E2XXJRX | FN3450-8-112-E2XXJRX | FN3442-8-112-E2XXJRX | FN3452-10-112-E2XXJRX | FN3446-8-44-E2XXJXX | FN3446-8-44-E2XXJXX | FN3458-10-44-E2XXJXX | FN3458-10-44-E2XXJXX | RWK3044-18-89-E0XXX | RWK305-17-KL | RWK5420-18-89-E0XXT | FN5060-24-84 | FN5420-18-33-E2FXT | FN3440-6-112-E2XXJRX | FN3450-6-112-E2XXJRX | FN3442-12-112-E2XXJRX | FN3452-15-112-E2XXJRX | FN3446-8-44-E2XXJXX | FN3446-8-44-E2XXJXX | FN3458-10-44-E2XXJXX | FN3458-8-44-E2XXJXX | RWK3044-12-88-E0XXX | RWK305-17-KL | RWK5420-18-89-E0XXT | FN5060-24-84 | FN5420-18-33-E2FXT | FN3288-16-44-C35-R65 | FN3287-16-44-C33-R65 | FN3288-16-44-C21-R65 | FN3288IT-16-44-C34-R65 | FN3120H-25-33 | FN3280H-16-29-69
6SL4113-0xA16-0xx0 | SINAMICS G220, 3AC 380...415/440...500V, 7.5kW | FN3440-11-113-E2FAJRX | FN3450-15-113-E2FAJRX | FN3442-12-112-E2XXJRX | FN3452-15-112-E2XXJRX | FN3446-8-44-E2XXJXX | FN3446-8-44-E2XXJXX | FN3458-15-33-E2FAJXX | FN3458-15-33-E2FAJXX | RWK3044-18-89-E0XXX | RWK305-24-KL | RWK5420-26-92-E0XXT | FN5060-24-84 | FN5420-26-33-E2FXT | FN3440-8-112-E2XXJRX | FN3450-8-112-E2XXJRX | FN3442-16-113-E2FAJRX | FN3452-20-113-E2FAJRX | FN3446-11-33-E2FAJXX | FN3446-11-33-E2FAJXX | FN3458-15-33-E2FAJXX | FN3458-10-44-E2XXJXX | RWK3044-18-89-E0XXX | RWK305-24-KL | RWK5420-26-92-E0XXT | FN5060-24-84 | FN5420-26-33-E2FXT | FN3288-20-33-C35-R65 | FN3287-20-33-C33-R65 | FN3288-20-33-C21-R65 | FN3288IT-20-33-C34-R65 | FN3120H-25-33 | FN3280H-25-33-69
6SL4113-0xA17-0xx0 | SINAMICS G220, 3AC 380...415/440...500V, 11kW | FN3440-11-113-E2FAJRX | FN3450-15-113-E2FAJRX | FN3442-16-113-E2FAJRX | FN3452-20-113-E2FAJRX | FN3446-11-33-E2FAJXX | FN3446-11-33-E2FAJXX | FN3458-20-33-E2FAJXX | FN3458-20-33-E2FAJXX | RWK3044-24-89-E0XXX | RWK305-32-KL | RWK5420-32-92-E0XXT | FN5060-30-99 | FN5420-32-33-E2FXT | FN3440-11-113-E2FAJRX | FN3450-15-113-E2FAJRX | FN3442-16-113-E2FAJRX | FN3452-20-113-E2FAJRX | FN3446-15-33-E2FAJXX | FN3446-15-33-E2FAJXX | FN3458-15-33-E2FAJXX | FN3458-15-33-E2FAJXX | RWK3044-24-89-E0XXX | RWK305-32-KL | RWK5420-32-92-E0XXT | FN5060-30-99 | FN5420-32-33-E2FXT | FN3288-25-33-C35-R65 | FN3287-25-33-C33-R65 | FN3288-25-33-C21-R65 | FN3288IT-25-33-C34-R65 | FN3120H-25-33 | FN3280H-25-33-69
6SL4113-0xA18-0xx0 | SINAMICS G220, 3AC 380...415/440...500V, 15kW | FN3440-15-113-E2FAJRX | FN3450-19-113-E2FAJRX | FN3442-20-113-E2FAJRX | FN3452-25-113-E2FAJRX | FN3446-15-33-E2FAJXX | FN3446-15-33-E2FAJXX | FN3458-25-33-E2FAJXX | FN3458-25-33-E2FAJXX | RWK3044-35-92-E0XXX | RWK305-45-KL | RWK5420-38-92-E0XXT | FN5060-45-99 | FN5420-38-33-E2FXT | FN3440-15-113-E2FAJRX | FN3450-19-113-E2FAJRX | FN3442-24-113-E2FAJRX | FN3452-30-113-E2FAJRX | FN3446-19-33-E2FAJXX | FN3446-19-33-E2FAJXX | FN3458-25-33-E2FAJXX | FN3458-20-33-E2FAJXX | RWK3044-30-92-E0XXX | RWK305-45-KL | RWK5420-45-92-E0XXT | FN5060-45-99 | FN5420-45-34-E2FXT | FN3288-40-33-C35-R65 | FN3287-40-33-C33-R65 | FN3288-40-33-C21-R65 | FN3288IT-40-33-C34-R65 | FN3120H-50-53 | FN3280H-36-33-69
6SL4113-0xA20-0xx0 | SINAMICS G220, 3AC 380...415/440...500V, 18.5k | FN3440-19-113-E2FAJRX | FN3450-22-113-E2FAJRX | FN3442-24-113-E2FAJRX | FN3452-30-113-E2FAJRX | FN3446-19-33-E2FAJXX | FN3446-19-33-E2FAJXX | FN3458-30-33-E2FAJXX | FN3458-30-33-E2FAJXX | RWK3044-48-92-E0XXX | RWK305-45-KL | RWK5420-45-92-E0XXT | FN5060-45-99 | FN5420-45-34-E2FXT | FN3440-22-115-E2FAJRX | FN3450-22-113-E2FAJRX | FN3442-40-115-E2FAJRX | FN3452-50-115-E2FAJRX | FN3446-30-34-E2FAJXX | FN3446-30-34-E2FAJXX | FN3458-30-33-E2FAJXX | FN3458-25-33-E2FAJXX | RWK3044-48-92-E0XXX | RWK305-60-KL | RWK5420-60-92-E0XXT | FN5060-60-99 | FN5420-60-34-E2FXT | FN3288-40-33-C35-R65 | FN3287-40-33-C33-R65 | FN3288-40-33-C21-R65 | FN3288IT-40-33-C34-R65 | FN3120H-50-53 | FN3280H-64-34-69
6SL4113-0xA21-0xx0 | SINAMICS G220, 3AC 380...415/440...500V, 22kW | FN3440-22-115-E2FAJRX | FN3450-30-115-E2FAJRX | FN3442-32-115-E2FAJRX | FN3452-40-115-E2FAJRX | FN3446-22-33-E2FAJXX | FN3446-22-33-E2FAJXX | FN3458-40-34-E2FAJXX | FN3458-40-34-E2FAJXX | RWK3044-48-92-E0XXX | RWK305-60-KL | RWK5420-60-92-E0XXT | FN5060-60-99 | FN5420-60-34-E2FXT | FN3440-30-115-E2FAJRX | FN3450-30-115-E2FAJRX | FN3442-40-115-E2FAJRX | FN3452-50-115-E2FAJRX | FN3446-30-34-E2FAJXX | FN3446-30-34-E2FAJXX | FN3458-40-34-E2FAJXX | FN3458-30-33-E2FAJXX | RWK3044-59-92-E0XXX | RWK305-60-KL | RWK5420-60-92-E0XXT | FN5060-60-99 | FN5420-60-34-E2FXT | FN3288-50-53-C35-R65 | FN3287-50-53-C33-R65 | FN3288-50-53-C21-R65 | FN3288IT-50-53-C34-R65 | FN3120H-50-53 | FN3280H-64-34-69
6SL4113-0xA23-0xx0 | SINAMICS G220, 3AC 380...415/440...500V, 30kW | FN3440-30-115-E2FAJRX | FN3450-37-115-E2FAJRX | FN3442-40-115-E2FAJRX | FN3452-50-115-E2FAJRX | FN3446-30-34-E2FAJXX | FN3446-30-34-E2FAJXX | FN3458-50-34-E2FAJXX | FN3458-50-34-E2FAJXX | RWK3044-72-99-E0XXX | RWK305-72-KL | RWK5420-75-99-E0XXT | FN5060-70-99 | FN5420-75-35-E2FXT | FN3440-30-115-E2FAJRX | FN3450-37-115-E2FAJRX | FN3442-48-115-E2FAJRX | FN3452-60-115-E2FAJRX | FN3446-37-34-E2FAJXX | FN3446-37-34-E2FAJXX | FN3458-50-34-E2FAJXX | FN3458-40-34-E2FAJXX | RWK3044-59-92-E0XXX | RWK305-72-KL | RWK5420-75-99-E0XXT | FN5060-70-99 | FN5420-75-35-E2FXT | FN3288-63-53-C35-R65 | FN3287-63-53-C33-R65 | FN3288-63-53-C21-R65 | FN3288IT-63-53-C34-R65 | FN3120H-80-35 | FN3280H-64-34-69
6SL4113-0xA24-0xx0 | SINAMICS G220, 3AC 380...415/440...500V, 37kW | FN3440-37-115-E2FAJRX | FN3450-45-115-E2FAJRX | FN3442-48-115-E2FAJRX | FN3452-60-115-E2FAJRX | FN3446-37-34-E2FAJXX | FN3446-37-34-E2FAJXX | FN3458-60-35-E2FAJXX | FN3458-60-35-E2FAJXX | RWK3044-88-99-E0XXX | RWK305-90-KL | RWK5420-90-99-E0XXT | FN5060-90-99 | FN5420-90-35-E2FXT | FN3440-45-115-E2FAJRX | FN3450-45-115-E2FAJRX | FN3442-60-115-E2FAJRX | FN3452-75-115-E2FAJRX | FN3446-55-35-E2FAJXX | FN3446-55-35-E2FAJXX | FN3458-60-35-E2FAJXX | FN3458-50-34-E2FAJXX | RWK3044-88-99-E0XXX | RWK305-110-KL | RWK5420-110-99-E0XXT | FN5060-110-99 | FN5420-110-35-E2FXT | FN3288-80-34-C35-R65 | FN3287-80-34-C33-R65 | FN3288-80-34-C21-R65 | FN3288IT-80-34-C34-R65 | FN3120H-80-35 | FN3280H-80-35-69
6SL4113-0xA26-0xx0 | SINAMICS G220, 3AC 380...415/440...500V, 45kW | FN3440-45-115-E2FAJRX | FN3450-55-115-E2FAJRX | FN3442-60-115-E2FAJRX | FN3452-75-115-E2FAJRX | FN3446-45-35-E2FAJXX | FN3446-45-35-E2FAJXX | FN3458-75-35-E2FAJXX | FN3458-75-35-E2FAJXX | RWK3044-88-99-E0XXX | RWK305-110-KL | RWK5420-110-99-E0XXT | FN5060-110-99 | FN5420-110-35-E2FXT | FN3440-55-115-E2FAJRX | FN3450-55-115-E2FAJRX | FN3442-80-115-E2FAJRX | FN3452-100-115-E2FAJRX | FN3446-55-35-E2FAJXX | FN3446-55-35-E2FAJXX | FN3458-75-35-E2FAJXX | FN3458-75-35-E2FAJXX | RWK3044-120-99-E0XXX | RWK305-124-KS | RWK5420-145-99-E0XXT | FN5060-150-99 | FN5420-145-99-E0XXT | FN3288-100-35-C35-R65 | FN3287-100-35-C33-R65 | FN3288-100-35-C21-R65 | FN3288IT-100-35-C34-R65 | FN3120H-110-35 | FN3280H-120-35-69
6SL4113-0xA27-0xx0 | SINAMICS G220, 3AC 380...415/440...500V, 55kW | FN3440-55-115-E2FAJRX | FN3450-75-115-E2FAJRX | FN3442-80-115-E2FAJRX | FN3452-100-115-E2FAJRX | FN3446-55-35-E2FAJXX | FN3446-55-35-E2FAJXX | FN3458-100-40-E2FAJXX | FN3458-100-40-E2FAJXX | RWK3044-120-99-E0XXX | RWK305-124-KS | RWK5420-145-99-E0XXT | FN5060-150-99 | FN5420-145-99-E0XXT | FN3440-75-116-E2FAJRX | FN3450-75-115-E2FAJRX | FN3442-100-116-E2FAJRX | FN3452-125-116-E2FAJRX | FN3446-75-40-E2FAJXX | FN3446-75-40-E2FAJXX | FN3458-100-40-E2FAJXX | FN3458-100-40-E2FAJXX | RWK3044-120-99-E0XXX | RWK305-143-KS | RWK5420-145-99-E0XXT | FN5060-150-99 | FN5420-145-99-E0XXT | FN3288-125-35-C35-R65 | FN3287-125-35-C33-R65 | FN3288-125-35-C21-R65 | FN3288IT-125-35-C34-R65 | FN3120H-110-35 | FN3280H-120-35-69
6SL4113-0xA08-2xx0 | SINAMICS G220, 3AC 380...415/440...500V, 1.1kW | FN3440-2-110-E2XXJRX | FN3450-4-112-E2XXJRX | FN3442-2-110-E2XXJRX | FN3452-3-110-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-5-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-3.5-88-E0XXX | RWK305-7.8-KL | RWK5420-5.9-88-E0XXT | FN5060-12-84 | FN5420-5.9-44-E2FXT | FN3440-1-110-E2XXJRX | FN3450-2-110-E2XXJRX | FN3442-2-110-E2XXJRX | FN3452-3-110-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-5-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-3.5-88-E0XXX | RWK305-7.8-KL | RWK5420-5.9-88-E0XXT | FN5060-12-84 | FN5420-5.9-44-E2FXT | FN3288-10-44-C34-R65 | FN3287-10-44-C28-R65 | FN3288-10-44-C21-R65 | FN3288IT-10-44-C34-R65 | FN3120H-25-33 | FN3280H-8-29-69
6SL4113-0xA10-2xx0 | SINAMICS G220, 3AC 380...415/440...500V, 1.5kW | FN3440-2-110-E2XXJRX | FN3450-4-112-E2XXJRX | FN3442-4-112-E2XXJRX | FN3452-5-112-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-5-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-6.5-88-E0XXX | RWK305-7.8-KL | RWK5420-5.9-88-E0XXT | FN5060-12-84 | FN5420-5.9-44-E2FXT | FN3440-1-110-E2XXJRX | FN3450-2-110-E2XXJRX | FN3442-4-112-E2XXJRX | FN3452-5-112-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-5-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-3.5-88-E0XXX | RWK305-7.8-KL | RWK5420-5.9-88-E0XXT | FN5060-12-84 | FN5420-5.9-44-E2FXT | FN3288-10-44-C34-R65 | FN3287-10-44-C28-R65 | FN3288-10-44-C21-R65 | FN3288IT-10-44-C34-R65 | FN3120H-25-33 | FN3280H-8-29-69
6SL4113-0xA11-2xx0 | SINAMICS G220, 3AC 380...415/440...500V, 2,2kW | FN3440-4-112-E2XXJRX | FN3450-6-112-E2XXJRX | FN3442-4-112-E2XXJRX | FN3452-5-112-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-5-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-6.5-88-E0XXX | RWK305-7.8-KL | RWK5420-10-88-E0XXT | FN5060-12-84 | FN5420-10-44-E2FXT | FN3440-2-110-E2XXJRX | FN3450-4-112-E2XXJRX | FN3442-4-112-E2XXJRX | FN3452-5-112-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-5-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-6.5-88-E0XXX | RWK305-7.8-KL | RWK5420-10-88-E0XXT | FN5060-12-84 | FN5420-10-44-E2FXT | FN3288-10-44-C34-R65 | FN3287-10-44-C28-R65 | FN3288-10-44-C21-R65 | FN3288IT-10-44-C34-R65 | FN3120H-25-33 | FN3280H-8-29-69
6SL4113-0xA12-2xx0 | SINAMICS G220, 3AC 380...415/440...500V, 3kW | FN3440-4-112-E2XXJRX | FN3450-6-112-E2XXJRX | FN3442-6-112-E2XXJRX | FN3452-8-112-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-8-44-E2XXJXX | FN3458-8-44-E2XXJXX | RWK3044-9-88-E0XXX | RWK305-10-KL | RWK5420-10-88-E0XXT | FN5060-12-84 | FN5420-10-44-E2FXT | FN3440-4-112-E2XXJRX | FN3450-4-112-E2XXJRX | FN3442-6-112-E2XXJRX | FN3452-8-112-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-5-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-6.5-88-E0XXX | RWK305-10-KL | RWK5420-10-88-E0XXT | FN5060-12-84 | FN5420-10-44-E2FXT | FN3288-10-44-C34-R65 | FN3287-10-44-C28-R65 | FN3288-10-44-C21-R65 | FN3288IT-10-44-C34-R65 | FN3120H-25-33 | FN3280H-8-29-69
6SL4113-0xA13-2xx0 | SINAMICS G220, 3AC 380...415/440...500V, 4kW | FN3440-4-112-E2XXJRX | FN3450-6-112-E2XXJRX | FN3442-6-112-E2XXJRX | FN3452-8-112-E2XXJRX | FN3446-4-44-E2XXJXX | FN3446-4-44-E2XXJXX | FN3458-8-44-E2XXJXX | FN3458-8-44-E2XXJXX | RWK3044-12-88-E0XXX | RWK305-14-KL | RWK5420-13-89-E0XXT | FN5060-12-84 | FN5420-13-33-E2FXT | FN3440-4-112-E2XXJRX | FN3450-6-112-E2XXJRX | FN3442-8-112-E2XXJRX | FN3452-10-112-E2XXJRX | FN3446-6-44-E2XXJXX | FN3446-6-44-E2XXJXX | FN3458-8-44-E2XXJXX | FN3458-5-44-E2XXJXX | RWK3044-9-88-E0XXX | RWK305-14-KL | RWK5420-13-89-E0XXT | FN5060-24-84 | FN5420-13-33-E2FXT | FN3288-10-44-C34-R65 | FN3287-10-44-C28-R65 | FN3288-10-44-C21-R65 | FN3288IT-10-44-C34-R65 | FN3120H-25-33 | FN3280H-16-29-69
6SL4113-0xA15-2xx0 | SINAMICS G220, 3AC 380...415/440...500V, 5.5kW | FN3440-6-112-E2XXJRX | FN3450-8-112-E2XXJRX | FN3442-8-112-E2XXJRX | FN3452-10-112-E2XXJRX | FN3446-8-44-E2XXJXX | FN3446-8-44-E2XXJXX | FN3458-10-44-E2XXJXX | FN3458-10-44-E2XXJXX | RWK3044-18-89-E0XXX | RWK305-17-KL | RWK5420-18-89-E0XXT | FN5060-24-84 | FN5420-18-33-E2FXT | FN3440-6-112-E2XXJRX | FN3450-6-112-E2XXJRX | FN3442-12-112-E2XXJRX | FN3452-15-112-E2XXJRX | FN3446-8-44-E2XXJXX | FN3446-8-44-E2XXJXX | FN3458-10-44-E2XXJXX | FN3458-8-44-E2XXJXX | RWK3044-12-88-E0XXX | RWK305-17-KL | RWK5420-18-89-E0XXT | FN5060-24-84 | FN5420-18-33-E2FXT | FN3288-16-44-C35-R65 | FN3287-16-44-C33-R65 | FN3288-16-44-C21-R65 | FN3288IT-16-44-C34-R65 | FN3120H-25-33 | FN3280H-16-29-69
6SL4113-0xA16-2xx0 | SINAMICS G220, 3AC 380...415/440...500V, 7.5kW | FN3440-11-113-E2FAJRX | FN3450-15-113-E2FAJRX | FN3442-12-112-E2XXJRX | FN3452-15-112-E2XXJRX | FN3446-8-44-E2XXJXX | FN3446-8-44-E2XXJXX | FN3458-15-33-E2FAJXX | FN3458-15-33-E2FAJXX | RWK3044-18-89-E0XXX | RWK305-24-KL | RWK5420-26-92-E0XXT | FN5060-24-84 | FN5420-26-33-E2FXT | FN3440-8-112-E2XXJRX | FN3450-8-112-E2XXJRX | FN3442-16-113-E2FAJRX | FN3452-20-113-E2FAJRX | FN3446-11-33-E2FAJXX | FN3446-11-33-E2FAJXX | FN3458-15-33-E2FAJXX | FN3458-10-44-E2XXJXX | RWK3044-18-89-E0XXX | RWK305-24-KL | RWK5420-26-92-E0XXT | FN5060-24-84 | FN5420-26-33-E2FXT | FN3288-20-33-C35-R65 | FN3287-20-33-C33-R65 | FN3288-20-33-C21-R65 | FN3288IT-20-33-C34-R65 | FN3120H-25-33 | FN3280H-25-33-69
6SL4113-0xA17-2xx0 | SINAMICS G220, 3AC 380...415/440...500V, 11kW | FN3440-11-113-E2FAJRX | FN3450-15-113-E2FAJRX | FN3442-16-113-E2FAJRX | FN3452-20-113-E2FAJRX | FN3446-11-33-E2FAJXX | FN3446-11-33-E2FAJXX | FN3458-20-33-E2FAJXX | FN3458-20-33-E2FAJXX | RWK3044-24-89-E0XXX | RWK305-32-KL | RWK5420-32-92-E0XXT | FN5060-30-99 | FN5420-32-33-E2FXT | FN3440-11-113-E2FAJRX | FN3450-15-113-E2FAJRX | FN3442-16-113-E2FAJRX | FN3452-20-113-E2FAJRX | FN3446-15-33-E2FAJXX | FN3446-15-33-E2FAJXX | FN3458-15-33-E2FAJXX | FN3458-15-33-E2FAJXX | RWK3044-24-89-E0XXX | RWK305-32-KL | RWK5420-32-92-E0XXT | FN5060-30-99 | FN5420-32-33-E2FXT | FN3288-25-33-C35-R65 | FN3287-25-33-C33-R65 | FN3288-25-33-C21-R65 | FN3288IT-25-33-C34-R65 | FN3120H-25-33 | FN3280H-25-33-69
6SL4113-0xA18-2xx0 | SINAMICS G220, 3AC 380...415/440...500V, 15kW | FN3440-15-113-E2FAJRX | FN3450-19-113-E2FAJRX | FN3442-20-113-E2FAJRX | FN3452-25-113-E2FAJRX | FN3446-15-33-E2FAJXX | FN3446-15-33-E2FAJXX | FN3458-25-33-E2FAJXX | FN3458-25-33-E2FAJXX | RWK3044-35-92-E0XXX | RWK305-45-KL | RWK5420-38-92-E0XXT | FN5060-45-99 | FN5420-38-33-E2FXT | FN3440-15-113-E2FAJRX | FN3450-19-113-E2FAJRX | FN3442-24-113-E2FAJRX | FN3452-30-113-E2FAJRX | FN3446-19-33-E2FAJXX | FN3446-19-33-E2FAJXX | FN3458-25-33-E2FAJXX | FN3458-20-33-E2FAJXX | RWK3044-30-92-E0XXX | RWK305-45-KL | RWK5420-45-92-E0XXT | FN5060-45-99 | FN5420-45-34-E2FXT | FN3288-40-33-C35-R65 | FN3287-40-33-C33-R65 | FN3288-40-33-C21-R65 | FN3288IT-40-33-C34-R65 | FN3120H-50-53 | FN3280H-36-33-69
6SL4113-0xA20-2xx0 | SINAMICS G220, 3AC 380...415/440...500V, 18.5kW | FN3440-19-113-E2FAJRX | FN3450-22-113-E2FAJRX | FN3442-24-113-E2FAJRX | FN3452-30-113-E2FAJRX | FN3446-19-33-E2FAJXX | FN3446-19-33-E2FAJXX | FN3458-30-33-E2FAJXX | FN3458-30-33-E2FAJXX | RWK3044-48-92-E0XXX | RWK305-45-KL | RWK5420-45-92-E0XXT | FN5060-45-99 | FN5420-45-34-E2FXT | FN3440-22-115-E2FAJRX | FN3450-22-113-E2FAJRX | FN3442-40-115-E2FAJRX | FN3452-50-115-E2FAJRX | FN3446-30-34-E2FAJXX | FN3446-30-34-E2FAJXX | FN3458-30-33-E2FAJXX | FN3458-25-33-E2FAJXX | RWK3044-48-92-E0XXX | RWK305-60-KL | RWK5420-60-92-E0XXT | FN5060-60-99 | FN5420-60-34-E2FXT | FN3288-40-33-C35-R65 | FN3287-40-33-C33-R65 | FN3288-40-33-C21-R65 | FN3288IT-40-33-C34-R65 | FN3120H-50-53 | FN3280H-64-34-69
6SL4113-0xA21-2xx0 | SINAMICS G220, 3AC 380...415/440...500V, 22kW | FN3440-22-115-E2FAJRX | FN3450-30-115-E2FAJRX | FN3442-32-115-E2FAJRX | FN3452-40-115-E2FAJRX | FN3446-22-33-E2FAJXX | FN3446-22-33-E2FAJXX | FN3458-40-34-E2FAJXX | FN3458-40-34-E2FAJXX | RWK3044-48-92-E0XXX | RWK305-60-KL | RWK5420-60-92-E0XXT | FN5060-60-99 | FN5420-60-34-E2FXT | FN3440-30-115-E2FAJRX | FN3450-30-115-E2FAJRX | FN3442-40-115-E2FAJRX | FN3452-50-115-E2FAJRX | FN3446-30-34-E2FAJXX | FN3446-30-34-E2FAJXX | FN3458-40-34-E2FAJXX | FN3458-30-33-E2FAJXX | RWK3044-59-92-E0XXX | RWK305-60-KL | RWK5420-60-92-E0XXT | FN5060-60-99 | FN5420-60-34-E2FXT | FN3288-50-53-C35-R65 | FN3287-50-53-C33-R65 | FN3288-50-53-C21-R65 | FN3288IT-50-53-C34-R65 | FN3120H-50-53 | FN3280H-64-34-69
6SL4113-0xA23-2xx0 | SINAMICS G220, 3AC 380...415/440...500V, 30kW | FN3440-30-115-E2FAJRX | FN3450-37-115-E2FAJRX | FN3442-40-115-E2FAJRX | FN3452-50-115-E2FAJRX | FN3446-30-34-E2FAJXX | FN3446-30-34-E2FAJXX | FN3458-50-34-E2FAJXX | FN3458-50-34-E2FAJXX | RWK3044-72-99-E0XXX | RWK305-72-KL | RWK5420-75-99-E0XXT | FN5060-70-99 | FN5420-75-35-E2FXT | FN3440-30-115-E2FAJRX | FN3450-37-115-E2FAJRX | FN3442-48-115-E2FAJRX | FN3452-60-115-E2FAJRX | FN3446-37-34-E2FAJXX | FN3446-37-34-E2FAJXX | FN3458-50-34-E2FAJXX | FN3458-40-34-E2FAJXX | RWK3044-59-92-E0XXX | RWK305-72-KL | RWK5420-75-99-E0XXT | FN5060-70-99 | FN5420-75-35-E2FXT | FN3288-63-53-C35-R65 | FN3287-63-53-C33-R65 | FN3288-63-53-C21-R65 | FN3288IT-63-53-C34-R65 | FN3120H-80-35 | FN3280H-64-34-69
6SL4113-0xA24-2xx0 | SINAMICS G220, 3AC 380...415/440...500V, 37kW | FN3440-37-115-E2FAJRX | FN3450-45-115-E2FAJRX | FN3442-48-115-E2FAJRX | FN3452-60-115-E2FAJRX | FN3446-37-34-E2FAJXX | FN3446-37-34-E2FAJXX | FN3458-60-35-E2FAJXX | FN3458-60-35-E2FAJXX | RWK3044-88-99-E0XXX | RWK305-90-KL | RWK5420-90-99-E0XXT | FN5060-90-99 | FN5420-90-35-E2FXT | FN3440-45-115-E2FAJRX | FN3450-45-115-E2FAJRX | FN3442-60-115-E2FAJRX | FN3452-75-115-E2FAJRX | FN3446-55-35-E2FAJXX | FN3446-55-35-E2FAJXX | FN3458-60-35-E2FAJXX | FN3458-50-34-E2FAJXX | RWK3044-88-99-E0XXX | RWK305-110-KL | RWK5420-110-99-E0XXT | FN5060-110-99 | FN5420-110-35-E2FXT | FN3288-80-34-C35-R65 | FN3287-80-34-C33-R65 | FN3288-80-34-C21-R65 | FN3288IT-80-34-C34-R65 | FN3120H-80-35 | FN3280H-80-35-69
6SL4113-0xA26-2xx0 | SINAMICS G220, 3AC 380...415/440...500V, 45kW | FN3440-45-115-E2FAJRX | FN3450-55-115-E2FAJRX | FN3442-60-115-E2FAJRX | FN3452-75-115-E2FAJRX | FN3446-45-35-E2FAJXX | FN3446-45-35-E2FAJXX | FN3458-75-35-E2FAJXX | FN3458-75-35-E2FAJXX | RWK3044-88-99-E0XXX | RWK305-110-KL | RWK5420-110-99-E0XXT | FN5060-110-99 | FN5420-110-35-E2FXT | FN3440-55-115-E2FAJRX | FN3450-55-115-E2FAJRX | FN3442-80-115-E2FAJRX | FN3452-100-115-E2FAJRX | FN3446-55-35-E2FAJXX | FN3446-55-35-E2FAJXX | FN3458-75-35-E2FAJXX | FN3458-75-35-E2FAJXX | RWK3044-120-99-E0XXX | RWK305-124-KS | RWK5420-145-99-E0XXT | FN5060-150-99 | FN5420-145-99-E0XXT | FN3288-100-35-C35-R65 | FN3287-100-35-C33-R65 | FN3288-100-35-C21-R65 | FN3288IT-100-35-C34-R65 | FN3120H-110-35 | FN3280H-120-35-69
6SL4113-0xA27-2xx0 | SINAMICS G220, 3AC 380...415/440...500V, 55kW | FN3440-55-115-E2FAJRX | FN3450-75-115-E2FAJRX | FN3442-80-115-E2FAJRX | FN3452-100-115-E2FAJRX | FN3446-55-35-E2FAJXX | FN3446-55-35-E2FAJXX | FN3458-100-40-E2FAJXX | FN3458-100-40-E2FAJXX | RWK3044-120-99-E0XXX | RWK305-124-KS | RWK5420-145-99-E0XXT | FN5060-150-99 | FN5420-145-99-E0XXT | FN3440-75-116-E2FAJRX | FN3450-75-115-E2FAJRX | FN3442-100-116-E2FAJRX | FN3452-125-116-E2FAJRX | FN3446-75-40-E2FAJXX | FN3446-75-40-E2FAJXX | FN3458-100-40-E2FAJXX | FN3458-100-40-E2FAJXX | RWK3044-120-99-E0XXX | RWK305-143-KS | RWK5420-145-99-E0XXT | FN5060-150-99 | FN5420-145-99-E0XXT | FN3288-125-35-C35-R65 | FN3287-125-35-C33-R65 | FN3288-125-35-C21-R65 | FN3288IT-125-35-C34-R65 | FN3120H-110-35 | FN3280H-120-35-69